## Data Sets
Datasets | Data Set Info
New Dataset
Monitoring Data
Breaker Data
Protection Settings
General Settings
Commands
Data Records
Module Data

## Register Access
Registers has to be accessed with in the Range for each Parameters. |  |  |  |  | Data Sets
Parameters | R/W Access | Register Range | Function Code | Remark
Monitoring Data
Status Parameters | R | 100001 - 100128 | 0x02
Monitoring Data
Metering Parameters | R | 300001 - 300326 | 0x04
Maintenance Parameters | R | 303001 - 303057 | 0x04
Breaker Data | R | 303501 - 303517 | 0x04
Records
Trip Record 1 to Trip Record 100 | R | 305001 - 310900 | 0x04
Event Record 1 to Event Record 400 | R | 311001 - 313400 | 0x04 | Module Pickup/Alarm Event Records & Other Event Records.
Maintenance Record 1 to Maintenance Record 5 | R | 315001 - 315045 | 0x04 | Maintenance Records
Product Info | R | 315126 - 315167 | 0x04 | Accessible over only RS-485 Modbus
Modules Data | R | 315251 - TBD | 0x04
User Mapped Parameters Configured Values
User Mapped Parameters | R | 304001 - 304125 | 0x04
Commands | RW | 1 - 16 | 0x01/0x05/0x15
Protection Settings
Set Group 1 | RW | 400001 - 400031 | 0x03/0x06/0x10
Reserved | RW | 400032 - 400250 | 0x03/0x06/0x10 | Rserved for Advance Protection Parameters in Mid & High Variant
Set Group 2 | RW | 400251 - 400281 | 0x03/0x06/0x10
Reserved | RW | 400282 - 400500 | 0x03/0x06/0x10 | Rserved for Advance Protection Parameters in Mid & High Variant
General Settings
System Settings | RW | 400501 - 400511 | 0x03/0x06/0x10
Unit Settings | RW | 400512 - 400567 | 0x03/0x06/0x10
Modbus Settings | RW | 400568 - 400573 | 0x03/0x06/0x10
PC-HMI Communication Settings | RW | 400574 - 400579 | 0x03/0x06/0x10
DI Settings | RW | 400580 - 400582 | 0x03/0x06/0x10
DO Settings | RW | 400583 - 400587 | 0x03/0x06/0x10
System Settings PC-HMI | RW | 400875-400877 | 0x03/0x06 | These Parmeters will be Modified only over PC-HMI and cannot be changed over Modbus
Module Settings | RW | 401000 - TBD | 0x03/0x06/0x10

## Monitoring Data
Timestamp data - Table 1
| Attribute Name | Size (in Byte) | [8 empty] | Data Sets |  | Complete data
| Year | 1 | [8 empty] | Register Access
| Month | 1
| Date | 1
| Hour | 1
| Minute | 1
| Second | 1
| mSecond | 2
| Attribute Name | Size (in Bytes) | Size (in Words) | Min Value | Max Value | Step Size | Multiplier | R/W Access | Register Address | Function Codes | Default Value | Units | Remarks
| Current Metering Data | [14 empty] | address | file name | word size | Min_Value | MaxL_Value | MaxH_Value | step_size
| R Phase Current | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300001 | 0x04 | - | A
| Y Phase Current | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300003 | 0x04 | - | A
| B Phase Current | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300005 | 0x04 | - | A
| N Phase Current | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300007 | 0x04 | - | A
| G Phase Current | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300009 | 0x04 | - | A
| Reserved | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300011 | 0x04 | - | A
| Reserved | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300013 | 0x04 | - | A
| R Phase Current Max | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300015 | 0x04 | - | A
| Y Phase Current Max | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300017 | 0x04 | - | A
| B Phase Current Max | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300019 | 0x04 | - | A
| N Phase Current Max | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300021 | 0x04 | - | A
| G Phase Current Max | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300023 | 0x04 | - | A
| Reserved | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300025 | 0x04 | - | A
| Reserved | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300027 | 0x04 | - | A
| R Phase Current Max Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 10 | R | 300029 | 0x04 | - | A
| Y Phase Current Max Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 10 | R | 300033 | 0x04 | - | A
| B Phase Current Max Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 10 | R | 300037 | 0x04 | - | A
| N Phase Current Max Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 10 | R | 300041 | 0x04 | - | A
| G Phase Current Max Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 10 | R | 300045 | 0x04 | - | A
| Reserved | 8 | 4 | 0 | 1260000 | 1 | 10 | R | 300049 | 0x04 | - | A
| Reserved | 8 | 4 | 0 | 1260000 | 1 | 10 | R | 300053 | 0x04 | - | A
| R Phase Current Min | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300057 | 0x04 | - | A
| Y Phase Current Min | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300059 | 0x04 | - | A
| B Phase Current Min | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300061 | 0x04 | - | A
| N Phase Current Min | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300063 | 0x04 | - | A
| G Phase Current Min | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300065 | 0x04 | - | A
| Reserved | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300067 | 0x04 | - | A
| Reserved | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300069 | 0x04 | - | A
| R Phase Current Min Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 10 | R | 300071 | 0x04 | - | A
| Y Phase Current Min Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 10 | R | 300075 | 0x04 | - | A
| B Phase Current Min Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 10 | R | 300079 | 0x04 | - | A
| N Phase Current Min Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 10 | R | 300083 | 0x04 | - | A
| G Phase Current Min Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 10 | R | 300087 | 0x04 | - | A
| Reserved | 8 | 4 | 0 | 1260000 | 1 | 10 | R | 300091 | 0x04 | - | A
| Reserved | 8 | 4 | 0 | 1260000 | 1 | 10 | R | 300095 | 0x04 | - | A
| Average Current | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300099 | 0x04 | - | A
| R Phase % Load Current | 2 | 1 | 0 | 2000 | 1 | 1 | R | 300101 | 0x04 | - | %
| Y Phase % Load Current | 2 | 1 | 0 | 2000 | 1 | 1 | R | 300102 | 0x04 | - | %
| B Phase % Load Current | 2 | 1 | 0 | 2000 | 1 | 1 | R | 300103 | 0x04 | - | %
| N Phase % Load Current | 2 | 1 | 0 | 2000 | 1 | 1 | R | 300104 | 0x04 | - | %
| Current unbalance R Phase | 2 | 1 | -200 | 200 | 1 | 1 | R | 300105 | 0x04 | - | %
| Current unbalance Y Phase | 2 | 1 | -200 | 200 | 1 | 1 | R | 300106 | 0x04 | - | %
| Current unbalance B Phase | 2 | 1 | -200 | 200 | 1 | 1 | R | 300107 | 0x04 | - | %
| Current unbalance Max | 2 | 1 | -200 | 200 | 1 | 1 | R | 300108 | 0x04 | - | %
| THD Current R | 2 | 1 | 0 | 5000 | 1 | 10 | R | 300109 | 0x04 | - | %
| THD Current Y | 2 | 1 | 0 | 5000 | 1 | 10 | R | 300110 | 0x04 | - | %
| THD Current B | 2 | 1 | 0 | 5000 | 1 | 10 | R | 300111 | 0x04 | - | %
| Total THD Current | 2 | 1 | 0 | 5000 | 1 | 10 | R | 300112 | 0x04 | - | %
Demand Current | R Phase Demand Current | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300113 | 0x04 | - | A
| Y Phase Demand Current | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300115 | 0x04 | - | A
| B Phase Demand Current | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300117 | 0x04 | - | A
| N Phase Demand Current | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300119 | 0x04 | - | A
| R Phase Demand Current Max | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300121 | 0x04 | - | A
| Y Phase Demand Current Max | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300123 | 0x04 | - | A
| B Phase Demand Current Max | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300125 | 0x04 | - | A
| N Phase Demand Current Max | 4 | 2 | 0 | 1260000 | 1 | 10 | R | 300127 | 0x04 | - | A
| R Phase Demand Current Max TimeStamp | 8 | 4 | 0 | Refer Table 1 | 1 | 1 | R | 300129 | 0x04 | - |  |  | Trip Time - Month | 1B
| Y Phase Demand Current Max TimeStamp | 8 | 4 | 0 | Refer Table 1 | 1 | 1 | R | 300133 | 0x04 | - |  |  | Trip Time - Date | 1B
| B Phase Demand Current Max TimeStamp | 8 | 4 | 0 | Refer Table 1 | 1 | 1 | R | 300137 | 0x04 | - |  |  | Trip Time - Hour | 1B
| N Phase Demand Current Max TimeStamp | 8 | 4 | 0 | Refer Table 1 | 1 | 1 | R | 300141 | 0x04 | - |  |  | Trip Time - Min | 1B
| R Phase Voltage | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300145 | 0x04 | - | V
| Y Phase Voltage | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300147 | 0x04 | - | V
| B Phase Voltage | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300149 | 0x04 | - | V
| R - Y Phase - Phase Voltage | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300151 | 0x04 | - | V
| Y - B Phase - Phase Voltage | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300153 | 0x04 | - | V
| B - R Phase - Phase Voltage | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300155 | 0x04 | - | V
| Residual Voltage | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300157 | 0x04 | - | V
| R Phase Voltage Max | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300159 | 0x04 | - | V
| Y Phase Voltage Max | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300161 | 0x04 | - | V
| B Phase Voltage Max | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300163 | 0x04 | - | V
| R - Y Phase - Phase Voltage Max | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300165 | 0x04 | - | V
| Y - B Phase - Phase Voltage Max | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300167 | 0x04 | - | V
| B - R Phase - Phase Voltage Max | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300169 | 0x04 | - | V
| Residual Voltage Max | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300171 | 0x04 | - | V
| R Phase Voltage Max Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 100 | R | 300173 | 0x04 | - | V
| Y Phase Voltage Max Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 100 | R | 300177 | 0x04 | - | V
| B Phase Voltage Max Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 100 | R | 300181 | 0x04 | - | V
| R - Y Phase - Phase Voltage Max Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 100 | R | 300185 | 0x04 | - | V
| Y - B Phase - Phase Voltage Max Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 100 | R | 300189 | 0x04 | - | V
| B - R Phase - Phase Voltage Max Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 100 | R | 300193 | 0x04 | - | V
| Residual Voltage Max Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 100 | R | 300197 | 0x04 | - | V
| R Phase Voltage Min | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300201 | 0x04 | - | V
| Y Phase Voltage Min | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300203 | 0x04 | - | V
| B Phase Voltage Min | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300205 | 0x04 | - | V
| R - Y Phase - Phase Voltage Min | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300207 | 0x04 | - | V
| Y - B Phase - Phase Voltage Min | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300209 | 0x04 | - | V
| B - R Phase - Phase Voltage Min | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300211 | 0x04 | - | V
| Residual Voltage Min | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300213 | 0x04 | - | V
| R Phase Voltage Min Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 100 | R | 300215 | 0x04 | - | V
| Y Phase Voltage Min Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 100 | R | 300219 | 0x04 | - | V
| B Phase Voltage Min Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 100 | R | 300223 | 0x04 | - | V
| R - Y Phase - Phase Voltage Min Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 100 | R | 300227 | 0x04 | - | V
| Y - B Phase - Phase Voltage Min Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 100 | R | 300231 | 0x04 | - | V
| B - R Phase - Phase Voltage Min Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 100 | R | 300235 | 0x04 | - | V
| Residual Voltage Min Time Stamp | 8 | 4 | 0 | Refer Table 1 | 1 | 100 | R | 300239 | 0x04 | - | V
| Phase - N Average Voltage | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300243 | 0x04 | - | V
| Line - Line Average Voltage | 4 | 2 | 0 | 120000 | 1 | 100 | R | 300245 | 0x04 | - | V
| Voltage unbalance R-N | 2 | 1 | -200 | 200 | 1 | 1 | R | 300247 | 0x04 | - | %
| Voltage unbalance Y-N | 2 | 1 | -200 | 200 | 1 | 1 | R | 300248 | 0x04 | - | %
| Voltage unbalance B-N | 2 | 1 | -200 | 200 | 1 | 1 | R | 300249 | 0x04 | - | %
| Voltage unbalance R-Y | 2 | 1 | -200 | 200 | 1 | 1 | R | 300250 | 0x04 | - | %
| Voltage unbalance Y-B | 2 | 1 | -200 | 200 | 1 | 1 | R | 300251 | 0x04 | - | %
| Voltage unbalance B-R | 2 | 1 | -200 | 200 | 1 | 1 | R | 300252 | 0x04 | - | %
| Voltage Max unbalance P-N | 2 | 1 | -200 | 200 | 1 | 1 | R | 300253 | 0x04 | - | %
| Voltage Max unbalance P-P | 2 | 1 | -200 | 200 | 1 | 1 | R | 300254 | 0x04 | - | %
| THD Voltage R | 2 | 1 | 0 | 5000 | 1 | 10 | R | 300255 | 0x04 | - | %
| THD Voltage Y | 2 | 1 | 0 | 5000 | 1 | 10 | R | 300256 | 0x04 | - | %
| THD Voltage B | 2 | 1 | 0 | 5000 | 1 | 10 | R | 300257 | 0x04 | - | %
| THD Total Voltage | 2 | 1 | 0 | 5000 | 1 | 10 | R | 300258 | 0x04 | - | %
| System Frequency | 2 | 1 | 0 | 12000 | 1 | 100 | R | 300259 | 0x04 | - | Hz
| Phase sequence | 2 | 1 | 123 | 132 | 1 | 1 | R | 300260 | 0x04 | -
| R Phase PF | 2 | 1 | -1000 | 1000 | 1 | 1000 | R | 300261 | 0x04 | -
| Y Phase PF | 2 | 1 | -1000 | 1000 | 1 | 1000 | R | 300262 | 0x04 | -
| B Phase PF | 2 | 1 | -1000 | 1000 | 1 | 1000 | R | 300263 | 0x04 | -
| System PF | 2 | 1 | -1000 | 1000 | 1 | 1000 | R | 300264 | 0x04 | -
| R Phase Active Power | 4 | 2 | -151200000 | 151200000 | 1 | 1 | R | 300265 | 0x04 | - | W
| Y Phase Active Power | 4 | 2 | -151200000 | 151200000 | 1 | 1 | R | 300267 | 0x04 | - | W
| B Phase Active Power | 4 | 2 | -151200000 | 151200000 | 1 | 1 | R | 300269 | 0x04 | - | W
| Total Active Power | 4 | 2 | -151200000 | 151200000 | 1 | 1 | R | 300271 | 0x04 | - | W
| R Phase Reactive Power | 4 | 2 | -151200000 | 151200000 | 1 | 1 | R | 300273 | 0x04 | - | Var
| Y Phase Reactive Power | 4 | 2 | -151200000 | 151200000 | 1 | 1 | R | 300275 | 0x04 | - | Var
| B Phase Reactive Power | 4 | 2 | -151200000 | 151200000 | 1 | 1 | R | 300277 | 0x04 | - | Var
| Total Reactive Power | 4 | 2 | -151200000 | 151200000 | 1 | 1 | R | 300279 | 0x04 | - | VAr
| R Phase App Power | 4 | 2 | 0 | 151200000 | 1 | 1 | R | 300281 | 0x04 | - | VA
| Y Phase App Power | 4 | 2 | 0 | 151200000 | 1 | 1 | R | 300283 | 0x04 | - | VA
| B Phase App Power | 4 | 2 | 0 | 151200000 | 1 | 1 | R | 300285 | 0x04 | - | VA
| Total App Power | 4 | 2 | 0 | 151200000 | 1 | 1 | R | 300287 | 0x04 | - | VA
| Total Active Energy | 4 | 2 | -2147483647 | 2147483647 | 1 | 1 | R | 300289 | 0x04 | - | Wh
| Total Reactive Energy | 4 | 2 | -2147483647 | 2147483647 | 1 | 1 | R | 300291 | 0x04 | - | kVarh
| Total App Energy | 4 | 2 | 0 | 2147483647 | 1 | 1 | R | 300293 | 0x04 | - | kVah
| Total Active Energy In | 4 | 2 | -2147483647 | 2147483647 | 1 | 1 | R | 300295 | 0x04 | - | Wh
| Total Reactive Energy In | 4 | 2 | -2147483647 | 2147483647 | 1 | 1 | R | 300297 | 0x04 | - | kVarh
| Total Active Energy out | 4 | 2 | -2147483647 | 2147483647 | 1 | 1 | R | 300299 | 0x04 | - | kWh
| Total Reactive Energy out | 4 | 2 | -2147483647 | 2147483647 | 1 | 1 | R | 300301 | 0x04 | - | kVarh
Demand Power | Demand Total Active Power | 4 | 2 | -151200000 | 151200000 | 1 | 1 | R | 300303 | 0x04 | - | W
| Demand Total Reactive Power | 4 | 2 | -151200000 | 151200000 | 1 | 1 | R | 300305 | 0x04 | - | VAr
| Demand Total App Power | 4 | 2 | 0 | 151200000 | 1 | 1 | R | 300307 | 0x04 | - | VA
| Demand Total Active Power Max | 4 | 2 | -151200000 | 151200000 | 1 | 1 | R | 300309 | 0x04 | - | W
| Demand Total Reactive Power Max | 4 | 2 | -151200000 | 151200000 | 1 | 1 | R | 300311 | 0x04 | - | VAr
| Demand Total App Power Max | 4 | 2 | 0 | 151200000 | 1 | 1 | R | 300313 | 0x04 | - | VA
| Demand Total Active Power Max TimeStamp | 8 | 4 | 0 | Refer Table 1 | 1 | 1 | R | 300315 | 0x04 | - |  |  | Trip Time - Sec | 1B
| Demand Total Reactive Power Max TimeStamp | 8 | 4 | 0 | Refer Table 1 | 1 | 1 | R | 300319 | 0x04 | - |  |  | Trip Time - mSec | 2B
| Demand Total App Power Max TimeStamp | 8 | 4 | 0 | Refer Table 1 | 1 | 1 | R | 300323 | 0x04 | -
Note on F58: Anil Garg: Range : Ref By NTNW
Note on F59: Anil Garg: Range : Ref By NTNW
Note on F60: Anil Garg: Range : Ref By NTNW
Note on F61: Anil Garg: Range : Ref By NTNW
Note on F119: Anil Garg: Range : Ref By NTNW
Note on F120: Anil Garg: Range : Ref By NTNW
Note on F121: Anil Garg: Range : Ref By NTNW
Note on F122: Anil Garg: Range : Ref By NTNW
Note on E124: Anil Garg: RYB
Note on F124: Anil Garg: RBY
Note on E129: Anil Garg: 6300 X 20 X 1200V
Note on E148: Anil Garg: 6300 X 20 X 1200V
Note on E149: Anil Garg: 6300 X 20 X 1200V
Note on E150: Anil Garg: 6300 X 20 X 1200V
Note on E151: Anil Garg: 6300 X 20 X 1200V
Note on E152: Anil Garg: 6300 X 20 X 1200V
Note on E153: Anil Garg: 6300 X 20 X 1200V

## Query_iTRP_1_2 (hidden)
Sr.No | Query
1 | 2 set groups needed in iTRP 1? As RTC not there, auto change set group setting not there, ARMS not there.
2 | Event recorder setting needed in iTRP1?
3 | MD settings required in iTRP2? Can be given for MD Current recording.
4 | Daylight saving feature? To be given in 2/3 or only 3?
5 | Fault counter to be given in iTRP1? Same is with fault counter clearing command
6 | Product info to commonised between RS485 and USB PC HMI?

## Breaker Data
Data Sets
Register Access
| Attribute Name | Size (in Bytes) | Size (in Words) | Min Value | Max Value | Step Size | Multiplier | R/W Access | Register Address | Function Codes | Default Value | Units | Remarks
| Breaker Status | 2 | 1 | 0 | 111 | - | 1 | R | 303501 | 0x04 | 0 | - | Bit0:On, Bit1:OFF, Bit2:TRIP
| Status Indication / Fault Status | 2 | 1 | 0 | 799 | - | 1 | R | 303502 | 0x04 | 0 | - | 0 - Normal 1 - Trip (Source as per Trip Record Source) 2 - Pickup (Source as per Event Record Source) 3 - Alarm (Source as per Event Record Source) /* Higher Byte - Type Lower Byte - Source */
| FSD Connection | 2 | 1 | 0 | 1 | - | 1 | R | 303503 | 0x04 | 1 | - | 0:Disconnected, 1:Connected
| Active Set Group | 2 | 1 | 0 | 1 | 1 | 1 | R | 303504 | 0x04 | 0 | - | 1 - Set Group1, 2-Set Group2
| RTC (Ready to Close ) Status | 2 | 1 | 0 | 20000 | 1 | 1 | R | 303505 | 0x04 | 0 | -
| CFI (Common Fault Indicator) Status | 2 | 1 | 0 | 20000 | 1 | 1 | R | 303506 | 0x04 | 0 | -
| CT Connection/disconnection | 2 | 1 | 0 | 1 | - | 1 | R | 303507 | 0x04 | 1 | - | R Phase - 0x0001, Y Phase, 0x0002, B Phase - 0x0004, N Phase - 0x0008
Communication Statistics | No of Received Message | 2 | 1 | 0 | 65535 | 1 | 1 | R | 303508 | 0x04 | 0 | -
| Number of received messages with error | 2 | 1 | 0 | 65535 | 1 | 1 | R | 303509 | 0x04 | 0 | -
| Number of responses | 2 | 1 | 0 | 65535 | 1 | 1 | R | 303510 | 0x04 | 0 | -
| Idle Time | 2 | 1 | 0 | 65535 | - | 1 | R | 303511 | 0x04 | 0 | - | 0 - 43200: s (upto 12 Hrs), 65535: > 12 Hrs
Fault Counter | L Trip | 2 | 1 | 0 | 20000 | 1 | 1 | R | 303512 | 0x04 | 0 | -
| S Trip | 2 | 1 | 0 | 20000 | 1 | 1 | R | 303513 | 0x04 | 0 | -
| I Trip | 2 | 1 | 0 | 20000 | 1 | 1 | R | 303514 | 0x04 | 0 | -
| G Trip | 2 | 1 | 0 | 20000 | 1 | 1 | R | 303515 | 0x04 | 0 | -
| Trip Due to Trip Unit | 2 | 1 | 0 | 20000 | 1 | 1 | R | 303516 | 0x04 | 0 | -
Breaker Operation Counter | Breaker Open operation | 2 | 1 | 0 | 20000 | 1 | 1 | R | 303517 | 0x04 | 0 | -
| Breaker Close operation | 2 | 1 | 0 | 20000 | 1 | 1 | R | 303518 | 0x04 | 0 | -
Contact wear | R Phase | 2 | 1 | 0 | 20000 | 1 | 10 | R | 303519 | 0x04 | 0 | %
| Y Phase | 2 | 1 | 0 | 20000 | 1 | 10 | R | 303520 | 0x05 | 0 | %
| B Phase | 2 | 1 | 0 | 20000 | 1 | 10 | R | 303521 | 0x06 | 0 | %
| N Phase | 2 | 1 | 0 | 20000 | 1 | 10 | R | 303522 | 0x07 | 0 | %
| Main MCU Healthiness Status | 2 | 1 | 0 | 20000 | 1 | 1 | R | 303523 | 0x04 | 0 | - | Used for Only Test Code. Reserved for Customer
Service Hours | Total Load duration since installation | 4 | 2 | 0 |  | 1 | 1 | R | 303524 | 0x04 | 0 | -
| Total Load duration since powerup | 4 | 2 | 0 |  | 1 | 1 | R | 303526 | 0x04 | 0 | -

## General Settings
Data Sets
Register Access
|  | Attribute Name | Data | Size(in Bytes) | Size(in Words) | Min Value | Max Value | Step Size | Multiplier | R/W Access | Register Address | Function Codes | Default Value | Units | Remarks
| System Settings | Frequency | 50, 60 Hz | 2 | 1 | 50 | 60 | 10 | 1 | RW | 400501 | 0x03,0x06,0x10 | 50 | Hz
|  | I_Frame | 800, 1600, 2500, 4000, 6300 A | 2 | 1 | 800 | 6300 | 1 | 1 | R | 400502 | 0x03,0x06,0x10 | 1600 | A | This Parameter cannot be modified over Modbus.
|  | Rated Current (In) | I Frame Rated Current 800 400, 630, 800 1600 800, 1000, 1250, 1600 2500 1250, 1600, 2000, 2500 4000 2000, 2500, 3200, 4000 6300 3200, 4000, 5000, 6300 | 2 | 1 | 400 | 6300 | - | - | R | 400503 | 0x03,0x06,0x10 | 1000 | A | This Parameter cannot be modified over Modbus.
|  | Nominal Voltage | 208, 220, 230, 240, 380, 400, 415, 440, 480, 500, 525, 550, 575, 600, 660, 690, 1000 V | 2 | 1 | 208 | 1000 | - | - | RW | 400504 | 0x03,0x06,0x10 | 400 | V | Ref by Schneider memory map
|  | Primary PT voltage | 380, 400, 415, 440, 480, 690 V | 2 | 1 | 380 | 690 | - | - | RW | 400505 | 0x03,0x06,0x10 | 400 | V | Settings received from ESE (6/3/24)
|  | Secondary PT voltage | 380, 400, 415, 440, 480, 690 V | 2 | 1 | 380 | 690 | - | - | RW | 400506 | 0x03,0x06,0x10 | 400 | V
|  | Maintenance Period | 1 to 12 Months | 2 | 1 | 1 | 12 | 1 | 1 | RW | 400507 | 0x03,0x06,0x10 | 6 | Month(s)
|  | Maintenance Enable/Disable | 0 - Disable, 1 - Enable | 2 | 1 | 0 | 1 | 1 | 1 | RW | 400508 | 0x03,0x06,0x10 | 0 | -
|  | Incoming | 0 -Top, 1 - Bottom | 2 | 1 | 0 | 1 | 1 | 1 | RW | 400509 | 0x03,0x06,0x10 | 0 | -
|  | Poles | 3 - 3 Poles, 4 - 4 Poles | 2 | 1 | 3 | 4 | 1 | 1 | RW | 400510 | 0x03,0x06,0x10 | 4 | Poles
|  | Phase Sequence | 0 - RYB, 1 - RBY, 2- NRYB, 3- NRBY, 4 - RYBN, 5 - RBYN | 2 | 1 | 0 | 5 | 1 | 1 | RW | 400511 | 0x03,0x06,0x10 | 2 | -
Unit Settings | RTC Settings | Date |  | 2 | 1 | 1 | 31 | 1 | 1 | RW | 400512 | 0x03,0x06,0x10 | 1
|  | Month |  | 2 | 1 | 1 | 12 | 1 | 1 | RW | 400513 | 0x03,0x06,0x10 | 1
|  | Year |  | 2 | 1 | 21 | 99 | 1 | 1 | RW | 400514 | 0x03,0x06,0x10 | 21
|  | Hour |  | 2 | 1 | 0 | 23 | 1 | 1 | RW | 400515 | 0x03,0x06,0x10 | 0
|  | Minute |  | 2 | 1 | 0 | 59 | 1 | 1 | RW | 400516 | 0x03,0x06,0x10 | 0
|  | Second |  | 2 | 1 | 0 | 59 | 1 | 1 | RW | 400517 | 0x03,0x06,0x10 | 0
|  | Reserved |  | 2 | 1 | 0 | 0 | 0 | 0 | RW | 400518 | 0x03,0x06,0x10 | 0
|  | Reserved |  | 2 | 1 | 0 | 0 | 0 | 0 | RW | 400519 | 0x03,0x06,0x10 | 0
|  | Reserved |  | 2 | 1 | 0 | 0 | 0 | 0 | RW | 400520 | 0x03,0x06,0x10 | 0
| Standard | Protection Curve Standard | 0 - IEC | 2 | 1 | 0 | 0 | - | - | RW | 400521 | 0x03,0x06,0x10 | 0
|  | Record Management | Bit0: Trip Record(0:OFF, 1:ON), Bit1: Event Pickup/Alarm (0:OFF, 1:ON), Bit2: Event Others (0:OFF, 1:ON) | 2 | 1 | 0 | 7 | 1 | 1 | RW | 400522 | 0x03,0x06,0x10 | 0
| Demand Settings | ENABLE | 0 - Disable, 1 - Enable | 2 | 1 | 0 | 1 | 1 | 1 | RW | 400523 | 0x03,0x06,0x10 | Disable | -
|  | MD Integration Period | 15, 30 Minutes | 2 | 1 | 15 | 30 | 15 | 1 | RW | 400524 | 0x03,0x06,0x10 | 15 | Minutes
|  | MD Sliding Interval | 5, 10, 15 Minutes | 2 | 1 | 5 | 15 | 5 | 1 | RW | 400525 | 0x03,0x06,0x10 | 5 | Minutes
|  | AutoChange SetGroup Enable / Disable | 0 - Disable, 1 - Enable | 2 | 1 | 0 | 1 | 1 | 1 | RW | 400526 | 0x03,0x06,0x10 | Disable | -
| SG1 to SG2 | Hour |  | 2 | 1 | 0 | 23 | 1 | 1 | RW | 400527 | 0x03,0x06,0x10 | 0 | -
|  | Minute |  | 2 | 1 | 0 | 59 | 1 | 1 | RW | 400528 | 0x03,0x06,0x10 | 0 | -
|  | Reserved |  | 2 | 1 | 0 | 59 | 1 | 1 | RW | 400529 | 0x03,0x06,0x10 | 0 | -
| SG2 to SG1 | Hour |  | 2 | 1 | 0 | 23 | 1 | 1 | RW | 400530 | 0x03,0x06,0x10 | 0 | -
|  | Minute |  | 2 | 1 | 0 | 59 | 1 | 1 | RW | 400531 | 0x03,0x06,0x10 | 0 | -
|  | Reserved |  | 2 | 1 | 0 | 59 | 1 | 1 | RW | 400532 | 0x03,0x06,0x10 | 0 | -
| Installation Date | Year |  | 2 | 1 | 21 | 99 | 1 | 1 | RW | 400533 | 0x03,0x06,0x10 | 21
|  | Month |  | 2 | 1 | 1 | 12 | 1 | 1 | RW | 400534 | 0x03,0x06,0x10 | 1
|  | Date |  | 2 | 1 | 1 | 31 | 1 | 1 | RW | 400535 | 0x03,0x06,0x10 | 1
| DayLight Saving Time (DST) | DST Enable / Disable | 0 - Disable, 1 - Enable | 2 | 1 | 0 | 1 | 1 | 1 | RW | 400536 | 0x03,0x06,0x10 | 0
|  | Start DST Month |  | 2 | 1 | 1 | 12 | 1 | 1 | RW | 400537 | 0x03,0x06,0x10 | 1
|  | Start DST Date |  | 2 | 1 | 1 | 31 | 1 | 1 | RW | 400538 | 0x03,0x06,0x10 | 1
|  | Start DST Hour |  | 2 | 1 | 0 | 23 | 1 | 1 | RW | 400539 | 0x03,0x06,0x10 | 0
|  | Start DST Minute |  | 2 | 1 | 0 | 59 | 1 | 1 | RW | 400540 | 0x03,0x06,0x10 | 0
|  | End DST Month |  | 2 | 1 | 1 | 12 | 1 | 1 | RW | 400541 | 0x03,0x06,0x10 | 1
|  | End DST Date |  | 2 | 1 | 1 | 31 | 1 | 1 | RW | 400542 | 0x03,0x06,0x10 | 1
|  | End DST Hour |  | 2 | 1 | 0 | 23 | 1 | 1 | RW | 400543 | 0x03,0x06,0x10 | 0
|  | End DST Minute |  | 2 | 1 | 0 | 59 | 1 | 1 | RW | 400544 | 0x03,0x06,0x10 | 0
| Display Scrolling Screen Selection | Current Metering Screen1 Visible | 0 - Disable, 1 - Enable | 2 | 1 | 0 | 1 | 1 | 1 | RW | 400545 | 0x03,0x06,0x10 | Enable | -
|  | Current Metering Screen1 Refresh Time | 1 - 10 S | 2 | 1 | 1 | 10 | 1 | 1 | RW | 400546 | 0x03,0x06,0x10 | 3 | Seconds
|  | Current Metering Screen2 Visible | 0 - Disable, 1 - Enable | 2 | 1 | 0 | 1 | 1 | 1 | RW | 400547 | 0x03,0x06,0x10 | Enable | -
|  | Current Metering Screen2 Refresh Time | 1 - 10 S | 2 | 1 | 1 | 10 | 1 | 1 | RW | 400548 | 0x03,0x06,0x10 | 3 | Seconds
|  | Voltage Ph-N Metering Screen Visible | 0 - Disable, 1 - Enable | 2 | 1 | 0 | 1 | 1 | 1 | RW | 400549 | 0x03,0x06,0x10 | Enable | -
|  | Voltage Ph-N Metering Screen Refresh Time | 1 - 10 S | 2 | 1 | 1 | 10 | 1 | 1 | RW | 400550 | 0x03,0x06,0x10 | 3 | Seconds
|  | Voltage Ph-Ph Metering Screen Visible | 0 - Disable, 1 - Enable | 2 | 1 | 0 | 1 | 1 | 1 | RW | 400551 | 0x03,0x06,0x10 | Disable | -
|  | Voltage Ph-Ph Metering Screen Refresh Time | 1 - 10 S | 2 | 1 | 1 | 10 | 1 | 1 | RW | 400552 | 0x03,0x06,0x10 | 1 | Seconds
|  | Frequency & P.F. Metering Screen Visible | 0 - Disable, 1 - Enable | 2 | 1 | 0 | 1 | 1 | 1 | RW | 400553 | 0x03,0x06,0x10 | Disable | -
|  | Frequency & P.F. Metering Screen Refresh Time | 1 - 10 S | 2 | 1 | 1 | 10 | 1 | 1 | RW | 400554 | 0x03,0x06,0x10 | 1 | Seconds
|  | Act Power Metering Screen Visible | 0 - Disable, 1 - Enable | 2 | 1 | 0 | 1 | 1 | 1 | RW | 400555 | 0x03,0x06,0x10 | Disable | -
|  | Act Power Metering Screen Refresh Time | 1 - 10 S | 2 | 1 | 1 | 10 | 1 | 1 | RW | 400556 | 0x03,0x06,0x10 | 1 | Seconds
|  | Rea Power Metering Screen Visible | 0 - Disable, 1 - Enable | 2 | 1 | 0 | 1 | 1 | 1 | RW | 400557 | 0x03,0x06,0x10 | Disable | -
|  | Rea Power Metering Screen Refresh Time | 1 - 10 S | 2 | 1 | 1 | 10 | 1 | 1 | RW | 400558 | 0x03,0x06,0x10 | 1 | Seconds
|  | App Power Metering Screen Visible | 0 - Disable, 1 - Enable | 2 | 1 | 0 | 1 | 1 | 1 | RW | 400559 | 0x03,0x06,0x10 | Disable | -
|  | App Power Metering Screen Refresh Time | 1 - 10 S | 2 | 1 | 1 | 10 | 1 | 1 | RW | 400560 | 0x03,0x06,0x10 | 1 | Seconds
|  | Energy Metering Screen Visible | 0 - Disable, 1 - Enable | 2 | 1 | 0 | 1 | 1 | 1 | RW | 400561 | 0x03,0x06,0x10 | Disable | -
|  | Energy Metering Screen Refresh Time | 1 - 10 S | 2 | 1 | 1 | 10 | 1 | 1 | RW | 400562 | 0x03,0x06,0x10 | 1 | Seconds
|  | Reserved | - | 2 | 1 | 0 | 1 | 1 | 1 | RW | 400563 | 0x03,0x06,0x10 | - | -
|  | Reserved | - | 2 | 1 | 1 | 10 | 1 | 1 | RW | 400564 | 0x03,0x06,0x10 | - | -
| Screen Timeout | Screen Navigation Timeout | 1 - 10 Minutes | 2 | 1 | 1 | 10 | 1 | 1 | RW | 400565 | 0x03,0x06,0x10 | 1 | Minutes
|  | Reserved | - | 2 | 1 | - | - | - | - | - | 400566 | - | - | -
|  | Reserved | - | 2 | 1 | - | - | - | - | - | 400567 | - | - | -
| Modbus Settings | Node Address |  | 2 | 1 | 1 | 247 | 1 | 1 | RW | 400568 | 0x03,0x06,0x10 | 1
|  | Parity | 0 = None, 1 = Odd, 2 = Even | 2 | 1 | 0 | 2 | 0 | 0 | RW | 400569 | 0x03,0x06,0x10 | 0
|  | Baud Rate | 24 - 2400, 48 - 4800, 96 - 9600, 192 - 19200, 384 - 38400, 576 - 57600, 1152 - 115200 bps | 2 | 1 | 24 | 1152 | 1 | 1/10 | RW | 400570 | 0x03,0x06,0x10 | 192
|  | Stop Bits | 1 - 1 Stop Bit, 2 - 2 Stop Bits | 2 | 1 | 1 | 2 | 0 | 0 | RW | 400571 | 0x03,0x06,0x10 | 1
|  | Timeout |  | 2 | 1 | 1 | 60 | 1 | 1 | RW | 400572 | 0x03,0x06,0x10 | 1 | Seconds
|  | Reserved |  | 2 | 1 | 0 | 0 | 0 | 0 | RW | 400573 | 0x03,0x06,0x10 | 0
| PC-HMI Communication Settings | Node Address |  | 2 | 1 | 1 | 247 | 1 | 1 | RW | 400574 | 0x03,0x06,0x10 | 1
|  | Parity | 0 = None, 1 = Odd, 2 = Even | 2 | 1 | 0 | 2 | 0 | 0 | RW | 400575 | 0x03,0x06,0x10 | 0
|  | Baud Rate | 24 - 2400, 48 - 4800, 96 - 9600, 192 - 19200, 384 - 38400, 576 - 57600, 1152 - 115200 bps | 2 | 1 | 24 | 1152 | 1 | 1/10 | RW | 400576 | 0x03,0x06,0x10 | 192
|  | Stop Bits | 1 - 1 Stop Bit, 2 - 2 Stop Bits | 2 | 1 | 1 | 2 | 0 | 0 | RW | 400577 | 0x03,0x06,0x10 | 1
|  | Timeout |  | 2 | 1 | 1 | 60 | 1 | 1 | RW | 400578 | 0x03,0x06,0x10 | 1 | Seconds
|  | Reserved |  | 2 | 1 | 0 | 0 | 0 | 0 | RW | 400579 | 0x03,0x06,0x10 | 0
| DI Settings | DI1 Trigger Type | 0 - Active High, 1 - Active Low | 2 | 1 | 0 | 1 | 1 | 1 | RW | 400580 | 0x03,0x06,0x10 | 0
|  | DI1 Input Source |  | 2 | 1 | 0 | 3 | 1 | 1 | RW | 400581 | 0x03,0x06,0x10 | 0 |  | Refer Table 1
|  | DI1 Validation Time |  | 2 | 1 | 0 | 60000 | 1 | 1 | RW | 400582 | 0x03,0x06,0x10 | 0 | mSec
| DO Settings | DI1 Trigger Type | 0 - Active High, 1 - Active Low | 2 | 1 | 0 | 1 | 1 | 1 | RW | 400583 | 0x03,0x06,0x10 | 0
|  | DO1 Input Source |  | 2 | 1 | 0 | 3 | 1 | 1 | RW | 400584 | 0x03,0x06,0x10 | 0
|  | DO1 Tag |  | 2 | 1 | 0 | 3 | 1 | 1 | RW | 400585 | 0x03,0x06,0x10 | 0 |  | Refer Table 2
|  | DO1 Output Type | 0 - Level, 1 - Pulse | 2 | 1 | 0 | 1 | 1 | 1 | RW | 400586 | 0x03,0x06,0x10 | 0
|  | DO1 Pulse Time |  | 2 | 1 | 0 | 60000 | 1 | 1 | RW | 400587 | 0x03,0x06,0x10 | 0 | mSec
Table 1
|  | DI Input Source |  | Value
|  | Other |  | 0
|  | Trip Reset DI |  | 1
|  | Breaker Close DI |  | 2
|  | Breaker Open DI |  | 3
Table 2
|  | DO Tag |  | Value
|  | Other |  | 0
|  | Trip DO |  | 1
|  | Alarm DO |  | 2
|  | Pickup DO |  | 3
| System Settings PC-HMI | System Setting Write Initiate / Factory Setting Write Initiate | 0:Disable, 1:Enable | 2 | 1 | 0 | 1 | 1 | 1 | RW | 400876 | 0x03,0x06 | 1 | - | These parameters are available over PC-HMI USB Communication.
|  | I_Frame | 800, 1600, 3200, 4000, 6300 A | 2 | 1 | 800 | 6300 | 1 | 1 | RW | 400877 | 0x03,0x06,0x10 | 1600 | A
|  | Rated Current (In) | I Frame Rated Current 800 400, 630, 800 1600 1000, 1250, 1600 3200 2000, 2500, 3200 4000 2000, 2500, 3200, 4000 6300 5000, 6300 | 2 | 1 | 400 | 6300 | - | - | RW | 400878 | 0x03,0x06,0x10 | 1600 | A
|  | System Setting Write FRAM | 1, 2, 3: I Frame & Rated Current new values will not be saved to FRAM. 0: I Frame & Rated Current new values will be saved to FRAM. | 2 | 1 | 0 | 3 | 1 | 1 | RW | 400879 | 0x03,0x06 | 0 | -

## Data Records
| Few no of records | min 25 | [8 empty] | Data Sets
Register Access
| Attribute Name | Size(in Bytes) | Size(in Words) | Min Value | Max Value | Step Size | Multiplier | R/W Access | Register Address | Function Codes | Default Value | Units | Remarks
Trip Records
Trip Records | Trip Record 1 | 118 | 59 | - | - | - | - | R | 305001 | 0x04 | - | - | Trip Record Parameters
| Trip Record 2 | 118 | 59 | - | - | - | - | R | 305060 | 0x04 | - | -
| Trip Record 3 | 118 | 59 | - | - | - | - | R | 305119 | 0x04 | - | -
| Trip Record 4 | 118 | 59 | - | - | - | - | R | 305178 | 0x04 | - | -
| Trip Record 5 | 118 | 59 | - | - | - | - | R | 305237 | 0x04 | - | -
| Trip Record 6 | 118 | 59 | - | - | - | - | R | 305296 | 0x04 | - | -
| Trip Record 7 | 118 | 59 | - | - | - | - | R | 305355 | 0x04 | - | -
| Trip Record 8 | 118 | 59 | - | - | - | - | R | 305414 | 0x04 | - | -
| Trip Record 9 | 118 | 59 | - | - | - | - | R | 305473 | 0x04 | - | -
| Trip Record 10 | 118 | 59 | - | - | - | - | R | 305532 | 0x04 | - | -
| Trip Record 11 | 118 | 59 | - | - | - | - | R | 305591 | 0x04 | - | -
| Trip Record 12 | 118 | 59 | - | - | - | - | R | 305650 | 0x04 | - | -
| Trip Record 13 | 118 | 59 | - | - | - | - | R | 305709 | 0x04 | - | -
| Trip Record 14 | 118 | 59 | - | - | - | - | R | 305768 | 0x04 | - | -
| Trip Record 15 | 118 | 59 | - | - | - | - | R | 305827 | 0x04 | - | -
| Trip Record 16 | 118 | 59 | - | - | - | - | R | 305886 | 0x04 | - | -
| Trip Record 17 | 118 | 59 | - | - | - | - | R | 305945 | 0x04 | - | -
| Trip Record 18 | 118 | 59 | - | - | - | - | R | 306004 | 0x04 | - | -
| Trip Record 19 | 118 | 59 | - | - | - | - | R | 306063 | 0x04 | - | -
| Trip Record 20 | 118 | 59 | - | - | - | - | R | 306122 | 0x04 | - | -
| Trip Record 21 | 118 | 59 | - | - | - | - | R | 306181 | 0x04 | - | -
| Trip Record 22 | 118 | 59 | - | - | - | - | R | 306240 | 0x04 | - | -
| Trip Record 23 | 118 | 59 | - | - | - | - | R | 306299 | 0x04 | - | -
| Trip Record 24 | 118 | 59 | - | - | - | - | R | 306358 | 0x04 | - | -
| Trip Record 25 | 118 | 59 | - | - | - | - | R | 306417 | 0x04 | - | -
| Trip Record 26 | 118 | 59 | - | - | - | - | R | 306476 | 0x04 | - | -
| Trip Record 27 | 118 | 59 | - | - | - | - | R | 306535 | 0x04 | - | -
| Trip Record 28 | 118 | 59 | - | - | - | - | R | 306594 | 0x04 | - | -
| Trip Record 29 | 118 | 59 | - | - | - | - | R | 306653 | 0x04 | - | -
| Trip Record 30 | 118 | 59 | - | - | - | - | R | 306712 | 0x04 | - | -
| Trip Record 31 | 118 | 59 | - | - | - | - | R | 306771 | 0x04 | - | -
| Trip Record 32 | 118 | 59 | - | - | - | - | R | 306830 | 0x04 | - | -
| Trip Record 33 | 118 | 59 | - | - | - | - | R | 306889 | 0x04 | - | -
| Trip Record 34 | 118 | 59 | - | - | - | - | R | 306948 | 0x04 | - | -
| Trip Record 35 | 118 | 59 | - | - | - | - | R | 307007 | 0x04 | - | -
| Trip Record 36 | 118 | 59 | - | - | - | - | R | 307066 | 0x04 | - | -
| Trip Record 37 | 118 | 59 | - | - | - | - | R | 307125 | 0x04 | - | -
| Trip Record 38 | 118 | 59 | - | - | - | - | R | 307184 | 0x04 | - | -
| Trip Record 39 | 118 | 59 | - | - | - | - | R | 307243 | 0x04 | - | -
| Trip Record 40 | 118 | 59 | - | - | - | - | R | 307302 | 0x04 | - | -
| Trip Record 41 | 118 | 59 | - | - | - | - | R | 307361 | 0x04 | - | -
| Trip Record 42 | 118 | 59 | - | - | - | - | R | 307420 | 0x04 | - | -
| Trip Record 43 | 118 | 59 | - | - | - | - | R | 307479 | 0x04 | - | -
| Trip Record 44 | 118 | 59 | - | - | - | - | R | 307538 | 0x04 | - | -
| Trip Record 45 | 118 | 59 | - | - | - | - | R | 307597 | 0x04 | - | -
| Trip Record 46 | 118 | 59 | - | - | - | - | R | 307656 | 0x04 | - | -
| Trip Record 47 | 118 | 59 | - | - | - | - | R | 307715 | 0x04 | - | -
| Trip Record 48 | 118 | 59 | - | - | - | - | R | 307774 | 0x04 | - | -
| Trip Record 49 | 118 | 59 | - | - | - | - | R | 307833 | 0x04 | - | -
| Trip Record 50 | 118 | 59 | - | - | - | - | R | 307892 | 0x04 | - | -
| Trip Record 51 | 118 | 59 | - | - | - | - | R | 307951 | 0x04 | - | -
| Trip Record 52 | 118 | 59 | - | - | - | - | R | 308010 | 0x04 | - | -
| Trip Record 53 | 118 | 59 | - | - | - | - | R | 308069 | 0x04 | - | -
| Trip Record 54 | 118 | 59 | - | - | - | - | R | 308128 | 0x04 | - | -
| Trip Record 55 | 118 | 59 | - | - | - | - | R | 308187 | 0x04 | - | -
| Trip Record 56 | 118 | 59 | - | - | - | - | R | 308246 | 0x04 | - | -
| Trip Record 57 | 118 | 59 | - | - | - | - | R | 308305 | 0x04 | - | -
| Trip Record 58 | 118 | 59 | - | - | - | - | R | 308364 | 0x04 | - | -
| Trip Record 59 | 118 | 59 | - | - | - | - | R | 308423 | 0x04 | - | -
| Trip Record 60 | 118 | 59 | - | - | - | - | R | 308482 | 0x04 | - | -
| Trip Record 61 | 118 | 59 | - | - | - | - | R | 308541 | 0x04 | - | -
| Trip Record 62 | 118 | 59 | - | - | - | - | R | 308600 | 0x04 | - | -
| Trip Record 63 | 118 | 59 | - | - | - | - | R | 308659 | 0x04 | - | -
| Trip Record 64 | 118 | 59 | - | - | - | - | R | 308718 | 0x04 | - | -
| Trip Record 65 | 118 | 59 | - | - | - | - | R | 308777 | 0x04 | - | -
| Trip Record 66 | 118 | 59 | - | - | - | - | R | 308836 | 0x04 | - | -
| Trip Record 67 | 118 | 59 | - | - | - | - | R | 308895 | 0x04 | - | -
| Trip Record 68 | 118 | 59 | - | - | - | - | R | 308954 | 0x04 | - | -
| Trip Record 69 | 118 | 59 | - | - | - | - | R | 309013 | 0x04 | - | -
| Trip Record 70 | 118 | 59 | - | - | - | - | R | 309072 | 0x04 | - | -
| Trip Record 71 | 118 | 59 | - | - | - | - | R | 309131 | 0x04 | - | -
| Trip Record 72 | 118 | 59 | - | - | - | - | R | 309190 | 0x04 | - | -
| Trip Record 73 | 118 | 59 | - | - | - | - | R | 309249 | 0x04 | - | -
| Trip Record 74 | 118 | 59 | - | - | - | - | R | 309308 | 0x04 | - | -
| Trip Record 75 | 118 | 59 | - | - | - | - | R | 309367 | 0x04 | - | -
| Trip Record 76 | 118 | 59 | - | - | - | - | R | 309426 | 0x04 | - | -
| Trip Record 77 | 118 | 59 | - | - | - | - | R | 309485 | 0x04 | - | -
| Trip Record 78 | 118 | 59 | - | - | - | - | R | 309544 | 0x04 | - | -
| Trip Record 79 | 118 | 59 | - | - | - | - | R | 309603 | 0x04 | - | -
| Trip Record 80 | 118 | 59 | - | - | - | - | R | 309662 | 0x04 | - | -
| Trip Record 81 | 118 | 59 | - | - | - | - | R | 309721 | 0x04 | - | -
| Trip Record 82 | 118 | 59 | - | - | - | - | R | 309780 | 0x04 | - | -
| Trip Record 83 | 118 | 59 | - | - | - | - | R | 309839 | 0x04 | - | -
| Trip Record 84 | 118 | 59 | - | - | - | - | R | 309898 | 0x04 | - | -
| Trip Record 85 | 118 | 59 | - | - | - | - | R | 309957 | 0x04 | - | -
| Trip Record 86 | 118 | 59 | - | - | - | - | R | 310016 | 0x04 | - | -
| Trip Record 87 | 118 | 59 | - | - | - | - | R | 310075 | 0x04 | - | -
| Trip Record 88 | 118 | 59 | - | - | - | - | R | 310134 | 0x04 | - | -
| Trip Record 89 | 118 | 59 | - | - | - | - | R | 310193 | 0x04 | - | -
| Trip Record 90 | 118 | 59 | - | - | - | - | R | 310252 | 0x04 | - | -
| Trip Record 91 | 118 | 59 | - | - | - | - | R | 310311 | 0x04 | - | -
| Trip Record 92 | 118 | 59 | - | - | - | - | R | 310370 | 0x04 | - | -
| Trip Record 93 | 118 | 59 | - | - | - | - | R | 310429 | 0x04 | - | -
| Trip Record 94 | 118 | 59 | - | - | - | - | R | 310488 | 0x04 | - | -
| Trip Record 95 | 118 | 59 | - | - | - | - | R | 310547 | 0x04 | - | -
| Trip Record 96 | 118 | 59 | - | - | - | - | R | 310606 | 0x04 | - | -
| Trip Record 97 | 118 | 59 | - | - | - | - | R | 310665 | 0x04 | - | -
| Trip Record 98 | 118 | 59 | - | - | - | - | R | 310724 | 0x04 | - | -
| Trip Record 99 | 118 | 59 | - | - | - | - | R | 310783 | 0x04 | - | -
| Trip Record 100 | 118 | 59 | - | - | - | - | R | 310842 | 0x04 | - | -
Event Records
Event Records | Event Record 1 | 12 | 6 | - | - | - | - | R | 311001 | 0x04 | - | - | Event Record Parameters
| Event Record 2 | 12 | 6 | - | - | - | - | R | 311007 | 0x04 | - | -
| Event Record 3 | 12 | 6 | - | - | - | - | R | 311013 | 0x04 | - | -
| Event Record 4 | 12 | 6 | - | - | - | - | R | 311019 | 0x04 | - | -
| Event Record 5 | 12 | 6 | - | - | - | - | R | 311025 | 0x04 | - | -
| Event Record 6 | 12 | 6 | - | - | - | - | R | 311031 | 0x04 | - | -
| Event Record 7 | 12 | 6 | - | - | - | - | R | 311037 | 0x04 | - | -
| Event Record 8 | 12 | 6 | - | - | - | - | R | 311043 | 0x04 | - | -
| Event Record 9 | 12 | 6 | - | - | - | - | R | 311049 | 0x04 | - | -
| Event Record 10 | 12 | 6 | - | - | - | - | R | 311055 | 0x04 | - | -
| Event Record 11 | 12 | 6 | - | - | - | - | R | 311061 | 0x04 | - | -
| Event Record 12 | 12 | 6 | - | - | - | - | R | 311067 | 0x04 | - | -
| Event Record 13 | 12 | 6 | - | - | - | - | R | 311073 | 0x04 | - | -
| Event Record 14 | 12 | 6 | - | - | - | - | R | 311079 | 0x04 | - | -
| Event Record 15 | 12 | 6 | - | - | - | - | R | 311085 | 0x04 | - | -
| Event Record 16 | 12 | 6 | - | - | - | - | R | 311091 | 0x04 | - | -
| Event Record 17 | 12 | 6 | - | - | - | - | R | 311097 | 0x04 | - | -
| Event Record 18 | 12 | 6 | - | - | - | - | R | 311103 | 0x04 | - | -
| Event Record 19 | 12 | 6 | - | - | - | - | R | 311109 | 0x04 | - | -
| Event Record 20 | 12 | 6 | - | - | - | - | R | 311115 | 0x04 | - | -
| Event Record 21 | 12 | 6 | - | - | - | - | R | 311121 | 0x04 | - | -
| Event Record 22 | 12 | 6 | - | - | - | - | R | 311127 | 0x04 | - | -
| Event Record 23 | 12 | 6 | - | - | - | - | R | 311133 | 0x04 | - | -
| Event Record 24 | 12 | 6 | - | - | - | - | R | 311139 | 0x04 | - | -
| Event Record 25 | 12 | 6 | - | - | - | - | R | 311145 | 0x04 | - | -
| Event Record 26 | 12 | 6 | - | - | - | - | R | 311151 | 0x04 | - | -
| Event Record 27 | 12 | 6 | - | - | - | - | R | 311157 | 0x04 | - | -
| Event Record 28 | 12 | 6 | - | - | - | - | R | 311163 | 0x04 | - | -
| Event Record 29 | 12 | 6 | - | - | - | - | R | 311169 | 0x04 | - | -
| Event Record 30 | 12 | 6 | - | - | - | - | R | 311175 | 0x04 | - | -
| Event Record 31 | 12 | 6 | - | - | - | - | R | 311181 | 0x04 | - | -
| Event Record 32 | 12 | 6 | - | - | - | - | R | 311187 | 0x04 | - | -
| Event Record 33 | 12 | 6 | - | - | - | - | R | 311193 | 0x04 | - | -
| Event Record 34 | 12 | 6 | - | - | - | - | R | 311199 | 0x04 | - | -
| Event Record 35 | 12 | 6 | - | - | - | - | R | 311205 | 0x04 | - | -
| Event Record 36 | 12 | 6 | - | - | - | - | R | 311211 | 0x04 | - | -
| Event Record 37 | 12 | 6 | - | - | - | - | R | 311217 | 0x04 | - | -
| Event Record 38 | 12 | 6 | - | - | - | - | R | 311223 | 0x04 | - | -
| Event Record 39 | 12 | 6 | - | - | - | - | R | 311229 | 0x04 | - | -
| Event Record 40 | 12 | 6 | - | - | - | - | R | 311235 | 0x04 | - | -
| Event Record 41 | 12 | 6 | - | - | - | - | R | 311241 | 0x04 | - | -
| Event Record 42 | 12 | 6 | - | - | - | - | R | 311247 | 0x04 | - | -
| Event Record 43 | 12 | 6 | - | - | - | - | R | 311253 | 0x04 | - | -
| Event Record 44 | 12 | 6 | - | - | - | - | R | 311259 | 0x04 | - | -
| Event Record 45 | 12 | 6 | - | - | - | - | R | 311265 | 0x04 | - | -
| Event Record 46 | 12 | 6 | - | - | - | - | R | 311271 | 0x04 | - | -
| Event Record 47 | 12 | 6 | - | - | - | - | R | 311277 | 0x04 | - | -
| Event Record 48 | 12 | 6 | - | - | - | - | R | 311283 | 0x04 | - | -
| Event Record 49 | 12 | 6 | - | - | - | - | R | 311289 | 0x04 | - | -
| Event Record 50 | 12 | 6 | - | - | - | - | R | 311295 | 0x04 | - | -
| Event Record 51 | 12 | 6 | - | - | - | - | R | 311301 | 0x04 | - | -
| Event Record 52 | 12 | 6 | - | - | - | - | R | 311307 | 0x04 | - | -
| Event Record 53 | 12 | 6 | - | - | - | - | R | 311313 | 0x04 | - | -
| Event Record 54 | 12 | 6 | - | - | - | - | R | 311319 | 0x04 | - | -
| Event Record 55 | 12 | 6 | - | - | - | - | R | 311325 | 0x04 | - | -
| Event Record 56 | 12 | 6 | - | - | - | - | R | 311331 | 0x04 | - | -
| Event Record 57 | 12 | 6 | - | - | - | - | R | 311337 | 0x04 | - | -
| Event Record 58 | 12 | 6 | - | - | - | - | R | 311343 | 0x04 | - | -
| Event Record 59 | 12 | 6 | - | - | - | - | R | 311349 | 0x04 | - | -
| Event Record 60 | 12 | 6 | - | - | - | - | R | 311355 | 0x04 | - | -
| Event Record 61 | 12 | 6 | - | - | - | - | R | 311361 | 0x04 | - | -
| Event Record 62 | 12 | 6 | - | - | - | - | R | 311367 | 0x04 | - | -
| Event Record 63 | 12 | 6 | - | - | - | - | R | 311373 | 0x04 | - | -
| Event Record 64 | 12 | 6 | - | - | - | - | R | 311379 | 0x04 | - | -
| Event Record 65 | 12 | 6 | - | - | - | - | R | 311385 | 0x04 | - | -
| Event Record 66 | 12 | 6 | - | - | - | - | R | 311391 | 0x04 | - | -
| Event Record 67 | 12 | 6 | - | - | - | - | R | 311397 | 0x04 | - | -
| Event Record 68 | 12 | 6 | - | - | - | - | R | 311403 | 0x04 | - | -
| Event Record 69 | 12 | 6 | - | - | - | - | R | 311409 | 0x04 | - | -
| Event Record 70 | 12 | 6 | - | - | - | - | R | 311415 | 0x04 | - | -
| Event Record 71 | 12 | 6 | - | - | - | - | R | 311421 | 0x04 | - | -
| Event Record 72 | 12 | 6 | - | - | - | - | R | 311427 | 0x04 | - | -
| Event Record 73 | 12 | 6 | - | - | - | - | R | 311433 | 0x04 | - | -
| Event Record 74 | 12 | 6 | - | - | - | - | R | 311439 | 0x04 | - | -
| Event Record 75 | 12 | 6 | - | - | - | - | R | 311445 | 0x04 | - | -
| Event Record 76 | 12 | 6 | - | - | - | - | R | 311451 | 0x04 | - | -
| Event Record 77 | 12 | 6 | - | - | - | - | R | 311457 | 0x04 | - | -
| Event Record 78 | 12 | 6 | - | - | - | - | R | 311463 | 0x04 | - | -
| Event Record 79 | 12 | 6 | - | - | - | - | R | 311469 | 0x04 | - | -
| Event Record 80 | 12 | 6 | - | - | - | - | R | 311475 | 0x04 | - | -
| Event Record 81 | 12 | 6 | - | - | - | - | R | 311481 | 0x04 | - | -
| Event Record 82 | 12 | 6 | - | - | - | - | R | 311487 | 0x04 | - | -
| Event Record 83 | 12 | 6 | - | - | - | - | R | 311493 | 0x04 | - | -
| Event Record 84 | 12 | 6 | - | - | - | - | R | 311499 | 0x04 | - | -
| Event Record 85 | 12 | 6 | - | - | - | - | R | 311505 | 0x04 | - | -
| Event Record 86 | 12 | 6 | - | - | - | - | R | 311511 | 0x04 | - | -
| Event Record 87 | 12 | 6 | - | - | - | - | R | 311517 | 0x04 | - | -
| Event Record 88 | 12 | 6 | - | - | - | - | R | 311523 | 0x04 | - | -
| Event Record 89 | 12 | 6 | - | - | - | - | R | 311529 | 0x04 | - | -
| Event Record 90 | 12 | 6 | - | - | - | - | R | 311535 | 0x04 | - | -
| Event Record 91 | 12 | 6 | - | - | - | - | R | 311541 | 0x04 | - | -
| Event Record 92 | 12 | 6 | - | - | - | - | R | 311547 | 0x04 | - | -
| Event Record 93 | 12 | 6 | - | - | - | - | R | 311553 | 0x04 | - | -
| Event Record 94 | 12 | 6 | - | - | - | - | R | 311559 | 0x04 | - | -
| Event Record 95 | 12 | 6 | - | - | - | - | R | 311565 | 0x04 | - | -
| Event Record 96 | 12 | 6 | - | - | - | - | R | 311571 | 0x04 | - | -
| Event Record 97 | 12 | 6 | - | - | - | - | R | 311577 | 0x04 | - | -
| Event Record 98 | 12 | 6 | - | - | - | - | R | 311583 | 0x04 | - | -
| Event Record 99 | 12 | 6 | - | - | - | - | R | 311589 | 0x04 | - | -
| Event Record 100 | 12 | 6 | - | - | - | - | R | 311595 | 0x04 | - | -
| Event Record 101 | 12 | 6 | - | - | - | - | R | 311601 | 0x04 | - | -
| Event Record 102 | 12 | 6 | - | - | - | - | R | 311607 | 0x04 | - | -
| Event Record 103 | 12 | 6 | - | - | - | - | R | 311613 | 0x04 | - | -
| Event Record 104 | 12 | 6 | - | - | - | - | R | 311619 | 0x04 | - | -
| Event Record 105 | 12 | 6 | - | - | - | - | R | 311625 | 0x04 | - | -
| Event Record 106 | 12 | 6 | - | - | - | - | R | 311631 | 0x04 | - | -
| Event Record 107 | 12 | 6 | - | - | - | - | R | 311637 | 0x04 | - | -
| Event Record 108 | 12 | 6 | - | - | - | - | R | 311643 | 0x04 | - | -
| Event Record 109 | 12 | 6 | - | - | - | - | R | 311649 | 0x04 | - | -
| Event Record 110 | 12 | 6 | - | - | - | - | R | 311655 | 0x04 | - | -
| Event Record 111 | 12 | 6 | - | - | - | - | R | 311661 | 0x04 | - | -
| Event Record 112 | 12 | 6 | - | - | - | - | R | 311667 | 0x04 | - | -
| Event Record 113 | 12 | 6 | - | - | - | - | R | 311673 | 0x04 | - | -
| Event Record 114 | 12 | 6 | - | - | - | - | R | 311679 | 0x04 | - | -
| Event Record 115 | 12 | 6 | - | - | - | - | R | 311685 | 0x04 | - | -
| Event Record 116 | 12 | 6 | - | - | - | - | R | 311691 | 0x04 | - | -
| Event Record 117 | 12 | 6 | - | - | - | - | R | 311697 | 0x04 | - | -
| Event Record 118 | 12 | 6 | - | - | - | - | R | 311703 | 0x04 | - | -
| Event Record 119 | 12 | 6 | - | - | - | - | R | 311709 | 0x04 | - | -
| Event Record 120 | 12 | 6 | - | - | - | - | R | 311715 | 0x04 | - | -
| Event Record 121 | 12 | 6 | - | - | - | - | R | 311721 | 0x04 | - | -
| Event Record 122 | 12 | 6 | - | - | - | - | R | 311727 | 0x04 | - | -
| Event Record 123 | 12 | 6 | - | - | - | - | R | 311733 | 0x04 | - | -
| Event Record 124 | 12 | 6 | - | - | - | - | R | 311739 | 0x04 | - | -
| Event Record 125 | 12 | 6 | - | - | - | - | R | 311745 | 0x04 | - | -
| Event Record 126 | 12 | 6 | - | - | - | - | R | 311751 | 0x04 | - | -
| Event Record 127 | 12 | 6 | - | - | - | - | R | 311757 | 0x04 | - | -
| Event Record 128 | 12 | 6 | - | - | - | - | R | 311763 | 0x04 | - | -
| Event Record 129 | 12 | 6 | - | - | - | - | R | 311769 | 0x04 | - | -
| Event Record 130 | 12 | 6 | - | - | - | - | R | 311775 | 0x04 | - | -
| Event Record 131 | 12 | 6 | - | - | - | - | R | 311781 | 0x04 | - | -
| Event Record 132 | 12 | 6 | - | - | - | - | R | 311787 | 0x04 | - | -
| Event Record 133 | 12 | 6 | - | - | - | - | R | 311793 | 0x04 | - | -
| Event Record 134 | 12 | 6 | - | - | - | - | R | 311799 | 0x04 | - | -
| Event Record 135 | 12 | 6 | - | - | - | - | R | 311805 | 0x04 | - | -
| Event Record 136 | 12 | 6 | - | - | - | - | R | 311811 | 0x04 | - | -
| Event Record 137 | 12 | 6 | - | - | - | - | R | 311817 | 0x04 | - | -
| Event Record 138 | 12 | 6 | - | - | - | - | R | 311823 | 0x04 | - | -
| Event Record 139 | 12 | 6 | - | - | - | - | R | 311829 | 0x04 | - | -
| Event Record 140 | 12 | 6 | - | - | - | - | R | 311835 | 0x04 | - | -
| Event Record 141 | 12 | 6 | - | - | - | - | R | 311841 | 0x04 | - | -
| Event Record 142 | 12 | 6 | - | - | - | - | R | 311847 | 0x04 | - | -
| Event Record 143 | 12 | 6 | - | - | - | - | R | 311853 | 0x04 | - | -
| Event Record 144 | 12 | 6 | - | - | - | - | R | 311859 | 0x04 | - | -
| Event Record 145 | 12 | 6 | - | - | - | - | R | 311865 | 0x04 | - | -
| Event Record 146 | 12 | 6 | - | - | - | - | R | 311871 | 0x04 | - | -
| Event Record 147 | 12 | 6 | - | - | - | - | R | 311877 | 0x04 | - | -
| Event Record 148 | 12 | 6 | - | - | - | - | R | 311883 | 0x04 | - | -
| Event Record 149 | 12 | 6 | - | - | - | - | R | 311889 | 0x04 | - | -
| Event Record 150 | 12 | 6 | - | - | - | - | R | 311895 | 0x04 | - | -
| Event Record 151 | 12 | 6 | - | - | - | - | R | 311901 | 0x04 | - | -
| Event Record 152 | 12 | 6 | - | - | - | - | R | 311907 | 0x04 | - | -
| Event Record 153 | 12 | 6 | - | - | - | - | R | 311913 | 0x04 | - | -
| Event Record 154 | 12 | 6 | - | - | - | - | R | 311919 | 0x04 | - | -
| Event Record 155 | 12 | 6 | - | - | - | - | R | 311925 | 0x04 | - | -
| Event Record 156 | 12 | 6 | - | - | - | - | R | 311931 | 0x04 | - | -
| Event Record 157 | 12 | 6 | - | - | - | - | R | 311937 | 0x04 | - | -
| Event Record 158 | 12 | 6 | - | - | - | - | R | 311943 | 0x04 | - | -
| Event Record 159 | 12 | 6 | - | - | - | - | R | 311949 | 0x04 | - | -
| Event Record 160 | 12 | 6 | - | - | - | - | R | 311955 | 0x04 | - | -
| Event Record 161 | 12 | 6 | - | - | - | - | R | 311961 | 0x04 | - | -
| Event Record 162 | 12 | 6 | - | - | - | - | R | 311967 | 0x04 | - | -
| Event Record 163 | 12 | 6 | - | - | - | - | R | 311973 | 0x04 | - | -
| Event Record 164 | 12 | 6 | - | - | - | - | R | 311979 | 0x04 | - | -
| Event Record 165 | 12 | 6 | - | - | - | - | R | 311985 | 0x04 | - | -
| Event Record 166 | 12 | 6 | - | - | - | - | R | 311991 | 0x04 | - | -
| Event Record 167 | 12 | 6 | - | - | - | - | R | 311997 | 0x04 | - | -
| Event Record 168 | 12 | 6 | - | - | - | - | R | 312003 | 0x04 | - | -
| Event Record 169 | 12 | 6 | - | - | - | - | R | 312009 | 0x04 | - | -
| Event Record 170 | 12 | 6 | - | - | - | - | R | 312015 | 0x04 | - | -
| Event Record 171 | 12 | 6 | - | - | - | - | R | 312021 | 0x04 | - | -
| Event Record 172 | 12 | 6 | - | - | - | - | R | 312027 | 0x04 | - | -
| Event Record 173 | 12 | 6 | - | - | - | - | R | 312033 | 0x04 | - | -
| Event Record 174 | 12 | 6 | - | - | - | - | R | 312039 | 0x04 | - | -
| Event Record 175 | 12 | 6 | - | - | - | - | R | 312045 | 0x04 | - | -
| Event Record 176 | 12 | 6 | - | - | - | - | R | 312051 | 0x04 | - | -
| Event Record 177 | 12 | 6 | - | - | - | - | R | 312057 | 0x04 | - | -
| Event Record 178 | 12 | 6 | - | - | - | - | R | 312063 | 0x04 | - | -
| Event Record 179 | 12 | 6 | - | - | - | - | R | 312069 | 0x04 | - | -
| Event Record 180 | 12 | 6 | - | - | - | - | R | 312075 | 0x04 | - | -
| Event Record 181 | 12 | 6 | - | - | - | - | R | 312081 | 0x04 | - | -
| Event Record 182 | 12 | 6 | - | - | - | - | R | 312087 | 0x04 | - | -
| Event Record 183 | 12 | 6 | - | - | - | - | R | 312093 | 0x04 | - | -
| Event Record 184 | 12 | 6 | - | - | - | - | R | 312099 | 0x04 | - | -
| Event Record 185 | 12 | 6 | - | - | - | - | R | 312105 | 0x04 | - | -
| Event Record 186 | 12 | 6 | - | - | - | - | R | 312111 | 0x04 | - | -
| Event Record 187 | 12 | 6 | - | - | - | - | R | 312117 | 0x04 | - | -
| Event Record 188 | 12 | 6 | - | - | - | - | R | 312123 | 0x04 | - | -
| Event Record 189 | 12 | 6 | - | - | - | - | R | 312129 | 0x04 | - | -
| Event Record 190 | 12 | 6 | - | - | - | - | R | 312135 | 0x04 | - | -
| Event Record 191 | 12 | 6 | - | - | - | - | R | 312141 | 0x04 | - | -
| Event Record 192 | 12 | 6 | - | - | - | - | R | 312147 | 0x04 | - | -
| Event Record 193 | 12 | 6 | - | - | - | - | R | 312153 | 0x04 | - | -
| Event Record 194 | 12 | 6 | - | - | - | - | R | 312159 | 0x04 | - | -
| Event Record 195 | 12 | 6 | - | - | - | - | R | 312165 | 0x04 | - | -
| Event Record 196 | 12 | 6 | - | - | - | - | R | 312171 | 0x04 | - | -
| Event Record 197 | 12 | 6 | - | - | - | - | R | 312177 | 0x04 | - | -
| Event Record 198 | 12 | 6 | - | - | - | - | R | 312183 | 0x04 | - | -
| Event Record 199 | 12 | 6 | - | - | - | - | R | 312189 | 0x04 | - | -
| Event Record 200 | 12 | 6 | - | - | - | - | R | 312195 | 0x04 | - | -
| Event Record 201 | 12 | 6 | - | - | - | - | R | 312201 | 0x04 | - | -
| Event Record 202 | 12 | 6 | - | - | - | - | R | 312207 | 0x04 | - | -
| Event Record 203 | 12 | 6 | - | - | - | - | R | 312213 | 0x04 | - | -
| Event Record 204 | 12 | 6 | - | - | - | - | R | 312219 | 0x04 | - | -
| Event Record 205 | 12 | 6 | - | - | - | - | R | 312225 | 0x04 | - | -
| Event Record 206 | 12 | 6 | - | - | - | - | R | 312231 | 0x04 | - | -
| Event Record 207 | 12 | 6 | - | - | - | - | R | 312237 | 0x04 | - | -
| Event Record 208 | 12 | 6 | - | - | - | - | R | 312243 | 0x04 | - | -
| Event Record 209 | 12 | 6 | - | - | - | - | R | 312249 | 0x04 | - | -
| Event Record 210 | 12 | 6 | - | - | - | - | R | 312255 | 0x04 | - | -
| Event Record 211 | 12 | 6 | - | - | - | - | R | 312261 | 0x04 | - | -
| Event Record 212 | 12 | 6 | - | - | - | - | R | 312267 | 0x04 | - | -
| Event Record 213 | 12 | 6 | - | - | - | - | R | 312273 | 0x04 | - | -
| Event Record 214 | 12 | 6 | - | - | - | - | R | 312279 | 0x04 | - | -
| Event Record 215 | 12 | 6 | - | - | - | - | R | 312285 | 0x04 | - | -
| Event Record 216 | 12 | 6 | - | - | - | - | R | 312291 | 0x04 | - | -
| Event Record 217 | 12 | 6 | - | - | - | - | R | 312297 | 0x04 | - | -
| Event Record 218 | 12 | 6 | - | - | - | - | R | 312303 | 0x04 | - | -
| Event Record 219 | 12 | 6 | - | - | - | - | R | 312309 | 0x04 | - | -
| Event Record 220 | 12 | 6 | - | - | - | - | R | 312315 | 0x04 | - | -
| Event Record 221 | 12 | 6 | - | - | - | - | R | 312321 | 0x04 | - | -
| Event Record 222 | 12 | 6 | - | - | - | - | R | 312327 | 0x04 | - | -
| Event Record 223 | 12 | 6 | - | - | - | - | R | 312333 | 0x04 | - | -
| Event Record 224 | 12 | 6 | - | - | - | - | R | 312339 | 0x04 | - | -
| Event Record 225 | 12 | 6 | - | - | - | - | R | 312345 | 0x04 | - | -
| Event Record 226 | 12 | 6 | - | - | - | - | R | 312351 | 0x04 | - | -
| Event Record 227 | 12 | 6 | - | - | - | - | R | 312357 | 0x04 | - | -
| Event Record 228 | 12 | 6 | - | - | - | - | R | 312363 | 0x04 | - | -
| Event Record 229 | 12 | 6 | - | - | - | - | R | 312369 | 0x04 | - | -
| Event Record 230 | 12 | 6 | - | - | - | - | R | 312375 | 0x04 | - | -
| Event Record 231 | 12 | 6 | - | - | - | - | R | 312381 | 0x04 | - | -
| Event Record 232 | 12 | 6 | - | - | - | - | R | 312387 | 0x04 | - | -
| Event Record 233 | 12 | 6 | - | - | - | - | R | 312393 | 0x04 | - | -
| Event Record 234 | 12 | 6 | - | - | - | - | R | 312399 | 0x04 | - | -
| Event Record 235 | 12 | 6 | - | - | - | - | R | 312405 | 0x04 | - | -
| Event Record 236 | 12 | 6 | - | - | - | - | R | 312411 | 0x04 | - | -
| Event Record 237 | 12 | 6 | - | - | - | - | R | 312417 | 0x04 | - | -
| Event Record 238 | 12 | 6 | - | - | - | - | R | 312423 | 0x04 | - | -
| Event Record 239 | 12 | 6 | - | - | - | - | R | 312429 | 0x04 | - | -
| Event Record 240 | 12 | 6 | - | - | - | - | R | 312435 | 0x04 | - | -
| Event Record 241 | 12 | 6 | - | - | - | - | R | 312441 | 0x04 | - | -
| Event Record 242 | 12 | 6 | - | - | - | - | R | 312447 | 0x04 | - | -
| Event Record 243 | 12 | 6 | - | - | - | - | R | 312453 | 0x04 | - | -
| Event Record 244 | 12 | 6 | - | - | - | - | R | 312459 | 0x04 | - | -
| Event Record 245 | 12 | 6 | - | - | - | - | R | 312465 | 0x04 | - | -
| Event Record 246 | 12 | 6 | - | - | - | - | R | 312471 | 0x04 | - | -
| Event Record 247 | 12 | 6 | - | - | - | - | R | 312477 | 0x04 | - | -
| Event Record 248 | 12 | 6 | - | - | - | - | R | 312483 | 0x04 | - | -
| Event Record 249 | 12 | 6 | - | - | - | - | R | 312489 | 0x04 | - | -
| Event Record 250 | 12 | 6 | - | - | - | - | R | 312495 | 0x04 | - | -
| Event Record 251 | 12 | 6 | - | - | - | - | R | 312501 | 0x04 | - | -
| Event Record 252 | 12 | 6 | - | - | - | - | R | 312507 | 0x04 | - | -
| Event Record 253 | 12 | 6 | - | - | - | - | R | 312513 | 0x04 | - | -
| Event Record 254 | 12 | 6 | - | - | - | - | R | 312519 | 0x04 | - | -
| Event Record 255 | 12 | 6 | - | - | - | - | R | 312525 | 0x04 | - | -
| Event Record 256 | 12 | 6 | - | - | - | - | R | 312531 | 0x04 | - | -
| Event Record 257 | 12 | 6 | - | - | - | - | R | 312537 | 0x04 | - | -
| Event Record 258 | 12 | 6 | - | - | - | - | R | 312543 | 0x04 | - | -
| Event Record 259 | 12 | 6 | - | - | - | - | R | 312549 | 0x04 | - | -
| Event Record 260 | 12 | 6 | - | - | - | - | R | 312555 | 0x04 | - | -
| Event Record 261 | 12 | 6 | - | - | - | - | R | 312561 | 0x04 | - | -
| Event Record 262 | 12 | 6 | - | - | - | - | R | 312567 | 0x04 | - | -
| Event Record 263 | 12 | 6 | - | - | - | - | R | 312573 | 0x04 | - | -
| Event Record 264 | 12 | 6 | - | - | - | - | R | 312579 | 0x04 | - | -
| Event Record 265 | 12 | 6 | - | - | - | - | R | 312585 | 0x04 | - | -
| Event Record 266 | 12 | 6 | - | - | - | - | R | 312591 | 0x04 | - | -
| Event Record 267 | 12 | 6 | - | - | - | - | R | 312597 | 0x04 | - | -
| Event Record 268 | 12 | 6 | - | - | - | - | R | 312603 | 0x04 | - | -
| Event Record 269 | 12 | 6 | - | - | - | - | R | 312609 | 0x04 | - | -
| Event Record 270 | 12 | 6 | - | - | - | - | R | 312615 | 0x04 | - | -
| Event Record 271 | 12 | 6 | - | - | - | - | R | 312621 | 0x04 | - | -
| Event Record 272 | 12 | 6 | - | - | - | - | R | 312627 | 0x04 | - | -
| Event Record 273 | 12 | 6 | - | - | - | - | R | 312633 | 0x04 | - | -
| Event Record 274 | 12 | 6 | - | - | - | - | R | 312639 | 0x04 | - | -
| Event Record 275 | 12 | 6 | - | - | - | - | R | 312645 | 0x04 | - | -
| Event Record 276 | 12 | 6 | - | - | - | - | R | 312651 | 0x04 | - | -
| Event Record 277 | 12 | 6 | - | - | - | - | R | 312657 | 0x04 | - | -
| Event Record 278 | 12 | 6 | - | - | - | - | R | 312663 | 0x04 | - | -
| Event Record 279 | 12 | 6 | - | - | - | - | R | 312669 | 0x04 | - | -
| Event Record 280 | 12 | 6 | - | - | - | - | R | 312675 | 0x04 | - | -
| Event Record 281 | 12 | 6 | - | - | - | - | R | 312681 | 0x04 | - | -
| Event Record 282 | 12 | 6 | - | - | - | - | R | 312687 | 0x04 | - | -
| Event Record 283 | 12 | 6 | - | - | - | - | R | 312693 | 0x04 | - | -
| Event Record 284 | 12 | 6 | - | - | - | - | R | 312699 | 0x04 | - | -
| Event Record 285 | 12 | 6 | - | - | - | - | R | 312705 | 0x04 | - | -
| Event Record 286 | 12 | 6 | - | - | - | - | R | 312711 | 0x04 | - | -
| Event Record 287 | 12 | 6 | - | - | - | - | R | 312717 | 0x04 | - | -
| Event Record 288 | 12 | 6 | - | - | - | - | R | 312723 | 0x04 | - | -
| Event Record 289 | 12 | 6 | - | - | - | - | R | 312729 | 0x04 | - | -
| Event Record 290 | 12 | 6 | - | - | - | - | R | 312735 | 0x04 | - | -
| Event Record 291 | 12 | 6 | - | - | - | - | R | 312741 | 0x04 | - | -
| Event Record 292 | 12 | 6 | - | - | - | - | R | 312747 | 0x04 | - | -
| Event Record 293 | 12 | 6 | - | - | - | - | R | 312753 | 0x04 | - | -
| Event Record 294 | 12 | 6 | - | - | - | - | R | 312759 | 0x04 | - | -
| Event Record 295 | 12 | 6 | - | - | - | - | R | 312765 | 0x04 | - | -
| Event Record 296 | 12 | 6 | - | - | - | - | R | 312771 | 0x04 | - | -
| Event Record 297 | 12 | 6 | - | - | - | - | R | 312777 | 0x04 | - | -
| Event Record 298 | 12 | 6 | - | - | - | - | R | 312783 | 0x04 | - | -
| Event Record 299 | 12 | 6 | - | - | - | - | R | 312789 | 0x04 | - | -
| Event Record 300 | 12 | 6 | - | - | - | - | R | 312795 | 0x04 | - | -
| Event Record 301 | 12 | 6 | - | - | - | - | R | 312801 | 0x04 | - | -
| Event Record 302 | 12 | 6 | - | - | - | - | R | 312807 | 0x04 | - | -
| Event Record 303 | 12 | 6 | - | - | - | - | R | 312813 | 0x04 | - | -
| Event Record 304 | 12 | 6 | - | - | - | - | R | 312819 | 0x04 | - | -
| Event Record 305 | 12 | 6 | - | - | - | - | R | 312825 | 0x04 | - | -
| Event Record 306 | 12 | 6 | - | - | - | - | R | 312831 | 0x04 | - | -
| Event Record 307 | 12 | 6 | - | - | - | - | R | 312837 | 0x04 | - | -
| Event Record 308 | 12 | 6 | - | - | - | - | R | 312843 | 0x04 | - | -
| Event Record 309 | 12 | 6 | - | - | - | - | R | 312849 | 0x04 | - | -
| Event Record 310 | 12 | 6 | - | - | - | - | R | 312855 | 0x04 | - | -
| Event Record 311 | 12 | 6 | - | - | - | - | R | 312861 | 0x04 | - | -
| Event Record 312 | 12 | 6 | - | - | - | - | R | 312867 | 0x04 | - | -
| Event Record 313 | 12 | 6 | - | - | - | - | R | 312873 | 0x04 | - | -
| Event Record 314 | 12 | 6 | - | - | - | - | R | 312879 | 0x04 | - | -
| Event Record 315 | 12 | 6 | - | - | - | - | R | 312885 | 0x04 | - | -
| Event Record 316 | 12 | 6 | - | - | - | - | R | 312891 | 0x04 | - | -
| Event Record 317 | 12 | 6 | - | - | - | - | R | 312897 | 0x04 | - | -
| Event Record 318 | 12 | 6 | - | - | - | - | R | 312903 | 0x04 | - | -
| Event Record 319 | 12 | 6 | - | - | - | - | R | 312909 | 0x04 | - | -
| Event Record 320 | 12 | 6 | - | - | - | - | R | 312915 | 0x04 | - | -
| Event Record 321 | 12 | 6 | - | - | - | - | R | 312921 | 0x04 | - | -
| Event Record 322 | 12 | 6 | - | - | - | - | R | 312927 | 0x04 | - | -
| Event Record 323 | 12 | 6 | - | - | - | - | R | 312933 | 0x04 | - | -
| Event Record 324 | 12 | 6 | - | - | - | - | R | 312939 | 0x04 | - | -
| Event Record 325 | 12 | 6 | - | - | - | - | R | 312945 | 0x04 | - | -
| Event Record 326 | 12 | 6 | - | - | - | - | R | 312951 | 0x04 | - | -
| Event Record 327 | 12 | 6 | - | - | - | - | R | 312957 | 0x04 | - | -
| Event Record 328 | 12 | 6 | - | - | - | - | R | 312963 | 0x04 | - | -
| Event Record 329 | 12 | 6 | - | - | - | - | R | 312969 | 0x04 | - | -
| Event Record 330 | 12 | 6 | - | - | - | - | R | 312975 | 0x04 | - | -
| Event Record 331 | 12 | 6 | - | - | - | - | R | 312981 | 0x04 | - | -
| Event Record 332 | 12 | 6 | - | - | - | - | R | 312987 | 0x04 | - | -
| Event Record 333 | 12 | 6 | - | - | - | - | R | 312993 | 0x04 | - | -
| Event Record 334 | 12 | 6 | - | - | - | - | R | 312999 | 0x04 | - | -
| Event Record 335 | 12 | 6 | - | - | - | - | R | 313005 | 0x04 | - | -
| Event Record 336 | 12 | 6 | - | - | - | - | R | 313011 | 0x04 | - | -
| Event Record 337 | 12 | 6 | - | - | - | - | R | 313017 | 0x04 | - | -
| Event Record 338 | 12 | 6 | - | - | - | - | R | 313023 | 0x04 | - | -
| Event Record 339 | 12 | 6 | - | - | - | - | R | 313029 | 0x04 | - | -
| Event Record 340 | 12 | 6 | - | - | - | - | R | 313035 | 0x04 | - | -
| Event Record 341 | 12 | 6 | - | - | - | - | R | 313041 | 0x04 | - | -
| Event Record 342 | 12 | 6 | - | - | - | - | R | 313047 | 0x04 | - | -
| Event Record 343 | 12 | 6 | - | - | - | - | R | 313053 | 0x04 | - | -
| Event Record 344 | 12 | 6 | - | - | - | - | R | 313059 | 0x04 | - | -
| Event Record 345 | 12 | 6 | - | - | - | - | R | 313065 | 0x04 | - | -
| Event Record 346 | 12 | 6 | - | - | - | - | R | 313071 | 0x04 | - | -
| Event Record 347 | 12 | 6 | - | - | - | - | R | 313077 | 0x04 | - | -
| Event Record 348 | 12 | 6 | - | - | - | - | R | 313083 | 0x04 | - | -
| Event Record 349 | 12 | 6 | - | - | - | - | R | 313089 | 0x04 | - | -
| Event Record 350 | 12 | 6 | - | - | - | - | R | 313095 | 0x04 | - | -
| Event Record 351 | 12 | 6 | - | - | - | - | R | 313101 | 0x04 | - | -
| Event Record 352 | 12 | 6 | - | - | - | - | R | 313107 | 0x04 | - | -
| Event Record 353 | 12 | 6 | - | - | - | - | R | 313113 | 0x04 | - | -
| Event Record 354 | 12 | 6 | - | - | - | - | R | 313119 | 0x04 | - | -
| Event Record 355 | 12 | 6 | - | - | - | - | R | 313125 | 0x04 | - | -
| Event Record 356 | 12 | 6 | - | - | - | - | R | 313131 | 0x04 | - | -
| Event Record 357 | 12 | 6 | - | - | - | - | R | 313137 | 0x04 | - | -
| Event Record 358 | 12 | 6 | - | - | - | - | R | 313143 | 0x04 | - | -
| Event Record 359 | 12 | 6 | - | - | - | - | R | 313149 | 0x04 | - | -
| Event Record 360 | 12 | 6 | - | - | - | - | R | 313155 | 0x04 | - | -
| Event Record 361 | 12 | 6 | - | - | - | - | R | 313161 | 0x04 | - | -
| Event Record 362 | 12 | 6 | - | - | - | - | R | 313167 | 0x04 | - | -
| Event Record 363 | 12 | 6 | - | - | - | - | R | 313173 | 0x04 | - | -
| Event Record 364 | 12 | 6 | - | - | - | - | R | 313179 | 0x04 | - | -
| Event Record 365 | 12 | 6 | - | - | - | - | R | 313185 | 0x04 | - | -
| Event Record 366 | 12 | 6 | - | - | - | - | R | 313191 | 0x04 | - | -
| Event Record 367 | 12 | 6 | - | - | - | - | R | 313197 | 0x04 | - | -
| Event Record 368 | 12 | 6 | - | - | - | - | R | 313203 | 0x04 | - | -
| Event Record 369 | 12 | 6 | - | - | - | - | R | 313209 | 0x04 | - | -
| Event Record 370 | 12 | 6 | - | - | - | - | R | 313215 | 0x04 | - | -
| Event Record 371 | 12 | 6 | - | - | - | - | R | 313221 | 0x04 | - | -
| Event Record 372 | 12 | 6 | - | - | - | - | R | 313227 | 0x04 | - | -
| Event Record 373 | 12 | 6 | - | - | - | - | R | 313233 | 0x04 | - | -
| Event Record 374 | 12 | 6 | - | - | - | - | R | 313239 | 0x04 | - | -
| Event Record 375 | 12 | 6 | - | - | - | - | R | 313245 | 0x04 | - | -
| Event Record 376 | 12 | 6 | - | - | - | - | R | 313251 | 0x04 | - | -
| Event Record 377 | 12 | 6 | - | - | - | - | R | 313257 | 0x04 | - | -
| Event Record 378 | 12 | 6 | - | - | - | - | R | 313263 | 0x04 | - | -
| Event Record 379 | 12 | 6 | - | - | - | - | R | 313269 | 0x04 | - | -
| Event Record 380 | 12 | 6 | - | - | - | - | R | 313275 | 0x04 | - | -
| Event Record 381 | 12 | 6 | - | - | - | - | R | 313281 | 0x04 | - | -
| Event Record 382 | 12 | 6 | - | - | - | - | R | 313287 | 0x04 | - | -
| Event Record 383 | 12 | 6 | - | - | - | - | R | 313293 | 0x04 | - | -
| Event Record 384 | 12 | 6 | - | - | - | - | R | 313299 | 0x04 | - | -
| Event Record 385 | 12 | 6 | - | - | - | - | R | 313305 | 0x04 | - | -
| Event Record 386 | 12 | 6 | - | - | - | - | R | 313311 | 0x04 | - | -
| Event Record 387 | 12 | 6 | - | - | - | - | R | 313317 | 0x04 | - | -
| Event Record 388 | 12 | 6 | - | - | - | - | R | 313323 | 0x04 | - | -
| Event Record 389 | 12 | 6 | - | - | - | - | R | 313329 | 0x04 | - | -
| Event Record 390 | 12 | 6 | - | - | - | - | R | 313335 | 0x04 | - | -
| Event Record 391 | 12 | 6 | - | - | - | - | R | 313341 | 0x04 | - | -
| Event Record 392 | 12 | 6 | - | - | - | - | R | 313347 | 0x04 | - | -
| Event Record 393 | 12 | 6 | - | - | - | - | R | 313353 | 0x04 | - | -
| Event Record 394 | 12 | 6 | - | - | - | - | R | 313359 | 0x04 | - | -
| Event Record 395 | 12 | 6 | - | - | - | - | R | 313365 | 0x04 | - | -
| Event Record 396 | 12 | 6 | - | - | - | - | R | 313371 | 0x04 | - | -
| Event Record 397 | 12 | 6 | - | - | - | - | R | 313377 | 0x04 | - | -
| Event Record 398 | 12 | 6 | - | - | - | - | R | 313383 | 0x04 | - | -
| Event Record 399 | 12 | 6 | - | - | - | - | R | 313389 | 0x04 | - | -
| Event Record 400 | 12 | 6 | - | - | - | - | R | 313395 | 0x04 | - | -
Maintenance Records
Maintenance Records | Maintenance Record 1 | 16 | 8 | - | - | - | - | R | 315001 | 0x04 | - | - | Maintenance Record Parameters
| Maintenance Record 2 | 16 | 8 | - | - | - | - | R | 315009 | 0x04 | - | -
| Maintenance Record 3 | 16 | 8 | - | - | - | - | R | 315017 | 0x04 | - | -
| Maintenance Record 4 | 16 | 8 | - | - | - | - | R | 315025 | 0x04 | - | -
| Maintenance Record 5 | 16 | 8 | - | - | - | - | R | 315033 | 0x04 | - | -

## Module Data
Data Sets
Register Access
| Attribute Name | Data | Size (in Bytes) | Size (in Words) | Min Value | Max Value | First Step Size | Further Step Size | Multiplier | R/W Access | Register Address | Function Codes | Default Value | Units | Remarks
TM-1
Product Information
| Product ID |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315251 | 0x04 | - | -
| Product S/R Number | 32 characters (ASCII: 0-9 / A-Z) | 32 | 16 | 0 | 4294967295 | 1 | 1 | 1 | R | 315253 | 0x04 | - | -
| Manufacture Day |  | 2 | 1 | 1 | 31 | 1 | 1 | 1 | R | 315269 | 0x04 | - | -
| Manufacture Month |  | 2 | 1 | 1 | 12 | 1 | 1 | 1 | R | 315270 | 0x04
| Manufacture Year |  | 2 | 1 | 21 | 99 | 1 | 1 | 1 | R | 315271 | 0x04
| Reserved |  | 4 | 2 | 0 | 0 | 0 | 0 | 0 | R | 315272 | 0x04
| Reserved |  | 4 | 2 | 0 | 0 | 0 | 0 | 0 | R | 315274 | 0x04
| Reserved |  | 4 | 2 | 0 | 0 | 0 | 0 | 0 | R | 315276 | 0x04
| Product Order code |  | 20 | 10 | 0 | 4294967295 | 1 | 1 | 1 | R | 315278 | 0x04
| Version Info | [10 empty] | 0x04
| HW Version |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315288 | 0x04
| SW Version |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315290 | 0x04
| Boot SW Version |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315292 | 0x04
| Module Data | [10 empty] | 0x04
| Temperature | [10 empty] | 0x04
| S1 Temperature (Set-1) | -25° to 150° C (Steps of 0.1°) | 2 | 1 | -250 | 1500 | 1 | 1 | 10 | R | 315294 | 0x04 | - | -
| S2 Temperature (Set-1) | -25° to 150° C (Steps of 0.1°) | 2 | 1 | -250 | 1500 | 1 | 1 | 10 | R | 315295 | 0x04 | - | -
| S3 Temperature (Set-1) | -25° to 150° C (Steps of 0.1°) | 2 | 1 | -250 | 1500 | 1 | 1 | 10 | R | 315296 | 0x04 | - | -
| S4 Temperature (Set-1) | -25° to 150° C (Steps of 0.1°) | 2 | 1 | -250 | 1500 | 1 | 1 | 10 | R | 315297 | 0x04 | - | -
| S5 Temperature (Set-2) | -25° to 150° C (Steps of 0.1°) | 2 | 1 | -250 | 1500 | 1 | 1 | 10 | R | 315298 | 0x04 | - | -
| S6 Temperature (Set-2) | -25° to 150° C (Steps of 0.1°) | 2 | 1 | -250 | 1500 | 1 | 1 | 10 | R | 315299 | 0x04 | - | -
| S7 Temperature (Set-2) | -25° to 150° C (Steps of 0.1°) | 2 | 1 | -250 | 1500 | 1 | 1 | 10 | R | 315300 | 0x04 | - | -
| S8 Temperature (Set-2) | -25° to 150° C (Steps of 0.1°) | 2 | 1 | -250 | 1500 | 1 | 1 | 10 | R | 315301 | 0x04 | - | -
| PT100 / PT1000 Temperature | -50° to 250° C (Steps of 0.1°) | 2 | 1 | -500 | 2500 | 1 | 1 | 10 | R | 315302 | 0x04 | - | -
Status
| S1 Status (Set-1) | 0: Normal, 1: Alarm, 2: Trip, 65535: Not Connected | 2 | 1 | 0 | 2 | 1 | 1 | 10 | R | 315303 | 0x04 | - | -
| S2 Status (Set-1) | 0: Normal, 1: Alarm, 2: Trip, 65535: Not Connected | 2 | 1 | 0 | 2 | 1 | 1 | 10 | R | 315304 | 0x04 | - | -
| S3 Status (Set-1) | 0: Normal, 1: Alarm, 2: Trip, 65535: Not Connected | 2 | 1 | 0 | 2 | 1 | 1 | 10 | R | 315305 | 0x04 | - | -
| S4 Status (Set-1) | 0: Normal, 1: Alarm, 2: Trip, 65535: Not Connected | 2 | 1 | 0 | 2 | 1 | 1 | 10 | R | 315306 | 0x04 | - | -
| S5 Status (Set-2) | 0: Normal, 1: Alarm, 2: Trip, 65535: Not Connected | 2 | 1 | 0 | 2 | 1 | 1 | 10 | R | 315307 | 0x04 | - | -
| S6 Status (Set-2) | 0: Normal, 1: Alarm, 2: Trip, 65535: Not Connected | 2 | 1 | 0 | 2 | 1 | 1 | 10 | R | 315308 | 0x04 | - | -
| S7 Status (Set-2) | 0: Normal, 1: Alarm, 2: Trip, 65535: Not Connected | 2 | 1 | 0 | 2 | 1 | 1 | 10 | R | 315309 | 0x04 | - | -
| S8 Status (Set-2) | 0: Normal, 1: Alarm, 2: Trip, 65535: Not Connected | 2 | 1 | 0 | 2 | 1 | 1 | 10 | R | 315310 | 0x04 | - | -
| PT100 / PT1000 Status | 0: Normal, 1: Alarm, 2: Trip, 65535: Not Connected | 2 | 1 | 0 | 2 | 1 | 1 | 10 | R | 315311 | 0x04 | - | -
TM-2
Product Information
| Product ID |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315312 | 0x04 | - | -
| Product S/R Number | 32 characters (ASCII: 0-9 / A-Z) | 32 | 16 | 0 | 4294967295 | 1 | 1 | 1 | R | 315314 | 0x04 | - | -
| Manufacture Day |  | 2 | 1 | 1 | 31 | 1 | 1 | 1 | R | 315330 | 0x04 | - | -
| Manufacture Month |  | 2 | 1 | 1 | 12 | 1 | 1 | 1 | R | 315331 | 0x04 | - | -
| Manufacture Year |  | 2 | 1 | 21 | 99 | 1 | 1 | 1 | R | 315332 | 0x04 | - | -
| Reserved |  | 4 | 2 | 0 | 0 | 0 | 0 | 0 | R | 315333 | 0x04 | - | -
| Reserved |  | 4 | 2 | 0 | 0 | 0 | 0 | 0 | R | 315335 | 0x04 | - | -
| Reserved |  | 4 | 2 | 0 | 0 | 0 | 0 | 0 | R | 315337 | 0x04 | - | -
| Product Order code |  | 20 | 10 | 0 | 4294967295 | 1 | 1 | 1 | R | 315339 | 0x04 | - | -
Version Info
| HW Version |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315349 | 0x04 | - | -
| SW Version |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315351 | 0x04 | - | -
| Boot SW Version |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315353 | 0x04 | - | -
Module Data
Temperature
| S1 Temperature (Set-1) | -25° to 150° C (Steps of 0.1°) | 2 | 1 | -250 | 1500 | 1 | 1 | 10 | R | 315355 | 0x04 | - | -
| S2 Temperature (Set-1) | -25° to 150° C (Steps of 0.1°) | 2 | 1 | -250 | 1500 | 1 | 1 | 10 | R | 315356 | 0x04 | - | -
| S3 Temperature (Set-1) | -25° to 150° C (Steps of 0.1°) | 2 | 1 | -250 | 1500 | 1 | 1 | 10 | R | 315357 | 0x04 | - | -
| S4 Temperature (Set-1) | -25° to 150° C (Steps of 0.1°) | 2 | 1 | -250 | 1500 | 1 | 1 | 10 | R | 315358 | 0x04 | - | -
| S5 Temperature (Set-2) | -25° to 150° C (Steps of 0.1°) | 2 | 1 | -250 | 1500 | 1 | 1 | 10 | R | 315359 | 0x04 | - | -
| S6 Temperature (Set-2) | -25° to 150° C (Steps of 0.1°) | 2 | 1 | -250 | 1500 | 1 | 1 | 10 | R | 315360 | 0x04 | - | -
| S7 Temperature (Set-2) | -25° to 150° C (Steps of 0.1°) | 2 | 1 | -250 | 1500 | 1 | 1 | 10 | R | 315361 | 0x04 | - | -
| S8 Temperature (Set-2) | -25° to 150° C (Steps of 0.1°) | 2 | 1 | -250 | 1500 | 1 | 1 | 10 | R | 315362 | 0x04 | - | -
| PT100 / PT1000 Temperature | -50° to 250° C (Steps of 0.1°) | 2 | 1 | -500 | 2500 | 1 | 1 | 10 | R | 315363 | 0x04 | - | -
Status
| S1 Status (Set-1) | 0: Normal, 1: Alarm, 2: Trip, 65535: Not Connected | 2 | 1 | 0 | 2 | 1 | 1 | 10 | R | 315364 | 0x04 | - | -
| S2 Status (Set-1) | 0: Normal, 1: Alarm, 2: Trip, 65535: Not Connected | 2 | 1 | 0 | 2 | 1 | 1 | 10 | R | 315365 | 0x04 | - | -
| S3 Status (Set-1) | 0: Normal, 1: Alarm, 2: Trip, 65535: Not Connected | 2 | 1 | 0 | 2 | 1 | 1 | 10 | R | 315366 | 0x04 | - | -
| S4 Status (Set-1) | 0: Normal, 1: Alarm, 2: Trip, 65535: Not Connected | 2 | 1 | 0 | 2 | 1 | 1 | 10 | R | 315367 | 0x04 | - | -
| S5 Status (Set-2) | 0: Normal, 1: Alarm, 2: Trip, 65535: Not Connected | 2 | 1 | 0 | 2 | 1 | 1 | 10 | R | 315368 | 0x04 | - | -
| S6 Status (Set-2) | 0: Normal, 1: Alarm, 2: Trip, 65535: Not Connected | 2 | 1 | 0 | 2 | 1 | 1 | 10 | R | 315369 | 0x04 | - | -
| S7 Status (Set-2) | 0: Normal, 1: Alarm, 2: Trip, 65535: Not Connected | 2 | 1 | 0 | 2 | 1 | 1 | 10 | R | 315370 | 0x04 | - | -
| S8 Status (Set-2) | 0: Normal, 1: Alarm, 2: Trip, 65535: Not Connected | 2 | 1 | 0 | 2 | 1 | 1 | 10 | R | 315371 | 0x04 | - | -
| PT100 / PT1000 Status | 0: Normal, 1: Alarm, 2: Trip, 65535: Not Connected | 2 | 1 | 0 | 2 | 1 | 1 | 10 | R | 315372 | 0x04 | - | -
DIO - 1
Product Information
| Product ID |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315373 | 0x04 | - | -
| Product S/R Number | 32 characters (ASCII: 0-9 / A-Z) | 32 | 16 | 0 | 4294967295 | 1 | 1 | 1 | R | 315375 | 0x04 | - | -
| Manufacture Day |  | 2 | 1 | 1 | 31 | 1 | 1 | 1 | R | 315391 | 0x04 | - | -
| Manufacture Month |  | 2 | 1 | 1 | 12 | 1 | 1 | 1 | R | 315392 | 0x04 | - | -
| Manufacture Year |  | 2 | 1 | 21 | 99 | 1 | 1 | 1 | R | 315393 | 0x04 | - | -
| Reserved |  | 4 | 2 | 0 | 0 | 0 | 0 | 0 | R | 315394 | 0x04 | - | -
| Reserved |  | 4 | 2 | 0 | 0 | 0 | 0 | 0 | R | 315396 | 0x04 | - | -
| Reserved |  | 4 | 2 | 0 | 0 | 0 | 0 | 0 | R | 315398 | 0x04 | - | -
| Product Order code |  | 20 | 10 | 0 | 4294967295 | 1 | 1 | 1 | R | 315400 | 0x04 | - | -
Version Info
| HW Version |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315410 | 0x04 | - | -
| SW Version |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315412 | 0x04 | - | -
| Boot SW Version |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315414 | 0x04 | - | -
Module Data
| DI-1 Status | 0:OFF, 1:ON | 2 | 1 | 0 | 1 | 1 | 1 | 1 | R | 315416 | 0x04 | - | -
| DI-2 Status | 0:OFF, 1:ON | 2 | 1 | 0 | 1 | 1 | 1 | 1 | R | 315417 | 0x04 | - | -
| DI-3 Status | 0:OFF, 1:ON | 2 | 1 | 0 | 1 | 1 | 1 | 1 | R | 315418 | 0x04 | - | -
| DO-1 Status | 0:OFF, 1:ON | 2 | 1 | 0 | 1 | 1 | 1 | 1 | R | 315419 | 0x04 | - | -
| DO-2 Status | 0:OFF, 1:ON | 2 | 1 | 0 | 1 | 1 | 1 | 1 | R | 315420 | 0x04 | - | -
DIO - 2
Product Information
| Product ID |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315421 | 0x04 | - | -
| Product S/R Number | 32 characters (ASCII: 0-9 / A-Z) | 32 | 16 | 0 | 4294967295 | 1 | 1 | 1 | R | 315423 | 0x04 | - | -
| Manufacture Day |  | 2 | 1 | 1 | 31 | 1 | 1 | 1 | R | 315439 | 0x04 | - | -
| Manufacture Month |  | 2 | 1 | 1 | 12 | 1 | 1 | 1 | R | 315440 | 0x04 | - | -
| Manufacture Year |  | 2 | 1 | 21 | 99 | 1 | 1 | 1 | R | 315441 | 0x04 | - | -
| Reserved |  | 4 | 2 | 0 | 0 | 0 | 0 | 0 | R | 315442 | 0x04 | - | -
| Reserved |  | 4 | 2 | 0 | 0 | 0 | 0 | 0 | R | 315444 | 0x04 | - | -
| Reserved |  | 4 | 2 | 0 | 0 | 0 | 0 | 0 | R | 315446 | 0x04 | - | -
| Product Order code |  | 20 | 10 | 0 | 4294967295 | 1 | 1 | 1 | R | 315448 | 0x04 | - | -
Version Info
| HW Version |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315458 | 0x04 | - | -
| SW Version |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315460 | 0x04 | - | -
| Boot SW Version |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315462 | 0x04 | - | -
Module Data
| DI-1 Status | 0:OFF, 1:ON | 2 | 1 | 0 | 1 | 1 | 1 | 1 | R | 315464 | 0x04 | - | -
| DI-2 Status | 0:OFF, 1:ON | 2 | 1 | 0 | 1 | 1 | 1 | 1 | R | 315465 | 0x04 | - | -
| DI-3 Status | 0:OFF, 1:ON | 2 | 1 | 0 | 1 | 1 | 1 | 1 | R | 315466 | 0x04 | - | -
| DO-1 Status | 0:OFF, 1:ON | 2 | 1 | 0 | 1 | 1 | 1 | 1 | R | 315467 | 0x04 | - | -
| DO-2 Status | 0:OFF, 1:ON | 2 | 1 | 0 | 1 | 1 | 1 | 1 | R | 315468 | 0x04 | - | -
DIO - 3
Product Information
| Product ID |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315469 | 0x04 | - | -
| Product S/R Number | 32 characters (ASCII: 0-9 / A-Z) | 32 | 16 | 0 | 4294967295 | 1 | 1 | 1 | R | 315471 | 0x04 | - | -
| Manufacture Day |  | 2 | 1 | 1 | 31 | 1 | 1 | 1 | R | 315487 | 0x04 | - | -
| Manufacture Month |  | 2 | 1 | 1 | 12 | 1 | 1 | 1 | R | 315488 | 0x04 | - | -
| Manufacture Year |  | 2 | 1 | 21 | 99 | 1 | 1 | 1 | R | 315489 | 0x04 | - | -
| Reserved |  | 4 | 2 | 0 | 0 | 0 | 0 | 0 | R | 315490 | 0x04 | - | -
| Reserved |  | 4 | 2 | 0 | 0 | 0 | 0 | 0 | R | 315492 | 0x04 | - | -
| Reserved |  | 4 | 2 | 0 | 0 | 0 | 0 | 0 | R | 315494 | 0x04 | - | -
| Product Order code |  | 20 | 10 | 0 | 4294967295 | 1 | 1 | 1 | R | 315496 | 0x04 | - | -
Version Info
| HW Version |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315506 | 0x04 | - | -
| SW Version |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315508 | 0x04 | - | -
| Boot SW Version |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315510 | 0x04 | - | -
Module Data
| DI-1 Status | 0:OFF, 1:ON | 2 | 1 | 0 | 1 | 1 | 1 | 1 | R | 315512 | 0x04 | - | -
| DI-2 Status | 0:OFF, 1:ON | 2 | 1 | 0 | 1 | 1 | 1 | 1 | R | 315513 | 0x04 | - | -
| DI-3 Status | 0:OFF, 1:ON | 2 | 1 | 0 | 1 | 1 | 1 | 1 | R | 315514 | 0x04 | - | -
| DO-1 Status | 0:OFF, 1:ON | 2 | 1 | 0 | 1 | 1 | 1 | 1 | R | 315515 | 0x04 | - | -
| DO-2 Status | 0:OFF, 1:ON | 2 | 1 | 0 | 1 | 1 | 1 | 1 | R | 315516 | 0x04 | - | -
DIO - 4
Product Information
| Product ID |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315517 | 0x04 | - | -
| Product S/R Number | 32 characters (ASCII: 0-9 / A-Z) | 32 | 16 | 0 | 4294967295 | 1 | 1 | 1 | R | 315519 | 0x04 | - | -
| Manufacture Day |  | 2 | 1 | 1 | 31 | 1 | 1 | 1 | R | 315535 | 0x04 | - | -
| Manufacture Month |  | 2 | 1 | 1 | 12 | 1 | 1 | 1 | R | 315536 | 0x04 | - | -
| Manufacture Year |  | 2 | 1 | 21 | 99 | 1 | 1 | 1 | R | 315537 | 0x04 | - | -
| Reserved |  | 4 | 2 | 0 | 0 | 0 | 0 | 0 | R | 315538 | 0x04 | - | -
| Reserved |  | 4 | 2 | 0 | 0 | 0 | 0 | 0 | R | 315540 | 0x04 | - | -
| Reserved |  | 4 | 2 | 0 | 0 | 0 | 0 | 0 | R | 315542 | 0x04 | - | -
| Product Order code |  | 20 | 10 | 0 | 4294967295 | 1 | 1 | 1 | R | 315544 | 0x04 | - | -
Version Info
| HW Version |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315554 | 0x04 | - | -
| SW Version |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315556 | 0x04 | - | -
| Boot SW Version |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315558 | 0x04 | - | -
Module Data
| DI-1 Status | 0:OFF, 1:ON | 2 | 1 | 0 | 1 | 1 | 1 | 1 | R | 315560 | 0x04 | - | -
| DI-2 Status | 0:OFF, 1:ON | 2 | 1 | 0 | 1 | 1 | 1 | 1 | R | 315561 | 0x04 | - | -
| DI-3 Status | 0:OFF, 1:ON | 2 | 1 | 0 | 1 | 1 | 1 | 1 | R | 315562 | 0x04 | - | -
| DO-1 Status | 0:OFF, 1:ON | 2 | 1 | 0 | 1 | 1 | 1 | 1 | R | 315563 | 0x04 | - | -
| DO-2 Status | 0:OFF, 1:ON | 2 | 1 | 0 | 1 | 1 | 1 | 1 | R | 315564 | 0x04 | - | -
Earth Leakage
Product Information
| Product ID |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315565 | 0x04 | - | -
| Product S/R Number | 32 characters (ASCII: 0-9 / A-Z) | 32 | 16 | 0 | 4294967295 | 1 | 1 | 1 | R | 315567 | 0x04 | - | -
| Manufacture Day |  | 2 | 1 | 1 | 31 | 1 | 1 | 1 | R | 315583 | 0x04 | - | -
| Manufacture Month |  | 2 | 1 | 1 | 12 | 1 | 1 | 1 | R | 315584 | 0x04 | - | -
| Manufacture Year |  | 2 | 1 | 21 | 99 | 1 | 1 | 1 | R | 315585 | 0x04 | - | -
| Reserved |  | 4 | 2 | 0 | 0 | 0 | 0 | 0 | R | 315586 | 0x04 | - | -
| Reserved |  | 4 | 2 | 0 | 0 | 0 | 0 | 0 | R | 315588 | 0x04 | - | -
| Reserved |  | 4 | 2 | 0 | 0 | 0 | 0 | 0 | R | 315590 | 0x04 | - | -
| Product Order code |  | 20 | 10 | 0 | 4294967295 | 1 | 1 | 1 | R | 315592 | 0x04 | - | -
Version Info
| HW Version |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315602 | 0x04 | - | -
| SW Version |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315604 | 0x04 | - | -
| Boot SW Version |  | 4 | 2 | 0 | 4294967295 | 1 | 1 | 1 | R | 315606 | 0x04 | - | -
Module Data
| EL Current |  | 4 | 2 | 0 | 3000 | 1 | 1 | 100 | R | 315608 | 0x04 | - | A
1 | Temperature/EL modules to log trip data irrespective of local/remote trip
2 | ETU to only log Event of remote tripping command
3 | Need to check on feasibility of timestamp logging in modules (battery)
4 | Feasibility of addition of 1 more DIP switch in EL module
5 | Format for trip logging at modules end to be finalised
6 | Trip record for modules to be added in Modules data
7 | Metering info for EL module to be added in modules data
8 | Ethernet module availability on ETU display along with IP address

## Protection Settings
|  |  | Complete | [8 empty] | Data Sets
Register Access
|  | Attribute Name | Data | Size (in Bytes) | Size (in Words) | Min Value | Max Value | First Step Size | Further Step Size | Multiplier | R/W Access | Register Address | Function Codes | Default Value | Units | Remarks
Current Protections (Set Group 1)
Current Protections (Set Group 1) | OverLoad Protection | Function | 0 : Protection Disable 1 : Alarm 2 : Trip 3 : Alarm + Trip | 2 | 1 | 0 | 3 | 1 | 1 | 1 | RW | 400001 | 0x03,0x06,0x10 | 0 | -
|  | Pickup (Ir) | 0.4 - 1 x In (Step: 0.01) | 2 | 1 | 40 | 100 | 1 | 1 | 1/100 | RW | 400002 | 0x03,0x06,0x10 | 60 | In (Amp)
|  | Prealarm | 0.5 - 0.95 x Ir (Step: 0.01) | 2 | 1 | 50 | 95 | 1 | 1 | 1/100 | RW | 400003 | 0x03,0x06,0x10 | 50 | Ir (Amp)
|  | Thermal Memory | 0:OFF, 20 min | 2 | 1 | 0 | 20 | - | - | 1 | RW | 400004 | 0x03,0x06,0x10 | 0 | -
|  | O/L Characteristic | 1: Extremely Inverse (I2T) 2: I Power 4 (I4T) 3: Very Inverse (VI) 4:Longtime Inverse (LI) 5: Standard Inverse (SI) | 2 | 1 | 1 | 5 | 1 | 1 | 1 | RW | 400005 | 0x03,0x06,0x10 | 0 | -
|  | Delay (@ 6 x Ir) | Range : 0.5, 1,2,4,6,12,18,24,30s. | 2 | 1 | 5 | 300 | - | - | 1/10 | RW | 400006 | 0x03,0x06,0x10 | 5 | Sec
| Short Circuit Protection | Function | 0 : Protection Disable 1 : Alarm 2 : Trip 3 : Alarm + Trip | 2 | 1 | 0 | 3 | 1 | 1 | 1 | RW | 400007 | 0x03,0x06,0x10 | 1 | -
|  | Double Selective | 0:Disable, 1:Enable | 2 | 1 | 0 | 1 | 1 | 1 | 1 | RW | 400008 | 0x03,0x06,0x10 | 0 | -
|  | Pickup High (Is) | 0.6 - 12 x In (Step of 0.05) | 2 | 1 | 60 | 1200 | 5 | 5 | 1/100 | RW | 400009 | 0x03,0x06,0x10 | 600 | In (Amp)
|  | Pickup Low (Is) | 0.6 - 12 x In (Step of 0.05) | 2 | 1 | 60 | 1200 | 5 | 5 | 1/100 | RW | 400010 | 0x03,0x06,0x10 | 600 | In (Amp)
|  | Prealarm | 0.5 - 0.95 x Is (Step: 0.05) | 2 | 1 | 50 | 95 | 5 | 5 | 1/100 | RW | 400011 | 0x03,0x06,0x10 | 50 | Is (Amp)
|  | I2T | 0:Disable, 1:Enable | 2 | 1 | 0 | 1 | 1 | 1 | 1 | RW | 400012 | 0x03,0x06,0x10 | 0 | -
|  | Delay High | 20-100-200-300-400ms | 2 | 1 | 20 | 400 | 80 | 100 | 1 | RW | 400013 | 0x03,0x06,0x10 | 400 | mSec
|  | Delay Low | 20-100-200-300-400ms | 2 | 1 | 20 | 400 | 80 | 100 | 1 | RW | 400014 | 0x03,0x06,0x10 | 400 | mSec
|  | Cold Load feature | 0:Disable, 1:Enable | 2 | 1 | 0 | 1 | 1 | 1 | 1 | RW | 400015 | 0x03,0x06,0x10 | 0 | -
|  | Cold Load Delay | 100ms to 10 Sec (Steps of 100ms) | 2 | 1 | 100 | 10000 | 100 | 100 | 1 | RW | 400016 | 0x03,0x06,0x10 | 1000 | mSec
|  | SC ZSI | 0:OFF, 1:IN, 2:OUT,3: BOTH | 2 | 1 | 0 | 3 | 1 | 1 | 1 | RW | 400017 | 0x03,0x06,0x10 | 0 | -
| Instantaneous Protection | Function | 0:Disable, 1:Enable | 2 | 1 | 0 | 1 | 1 | 1 | 1 | RW | 400018 | 0x03,0x06,0x10 | 1 | -
|  | Pickup | Range 1.5 In to 15 In 1.5 In to 10 In (Steps of 0.1 In) 10 In to 15 In (Steps of 1 In) | 2 | 1 | 15 | 150 | - | - | 1/10 | RW | 400019 | 0x03,0x06,0x10 | 1000 | In (Amp)
| Earth Fault Protection | Function | 0 : Protection Disable 1 : Alarm 2 : Trip 3 : Alarm + Trip | 2 | 1 | 0 | 3 | 1 | 1 | 1 | RW | 400020 | 0x03,0x06,0x10 | 0 | -
|  | Pickup (Ig) | 0.1 - 0.6 x In (Step 0.1) | 2 | 1 | 1 | 6 | 1 | 1 | 1/10 | RW | 400021 | 0x03,0x06,0x10 | 60 | In (Amp)
|  | Prealarm | 0.5 - 0.95 x Ig (Step: 0.05) | 2 | 1 | 50 | 95 | 5 | 5 | 1/100 | RW | 400022 | 0x03,0x06,0x10 | 80 | Ig (Amp)
|  | Cold Load feature | 0:Disable, 1:Enable | 2 | 1 | 0 | 1 | 1 | 1 | 1 | RW | 400023 | 0x03,0x06,0x10 | 0 | -
|  | Cold Load Delay | 100ms to 5 Sec (Steps of 100ms) | 2 | 1 | 100 | 5000 | 100 | 100 | 1 | RW | 400024 | 0x03,0x06,0x10 | 1000 | mSec
|  | E/F Characteristic (IDMT) | 0:Disable, 1:Enable | 2 | 1 | 0 | 1 | 1 | 1 | 1 | RW | 400025 | 0x03,0x06,0x10 | 0 | -
|  | IDMT Off Delay | 100ms to 1 Sec (Steps of 100ms) | 2 | 1 | 100 | 1000 | 100 | 100 | 1 | RW | 400026 | 0x03,0x06,0x10 | 400 | mSec
|  | IDMT On Delay | 100ms to 400ms (Steps of 100ms) | 2 | 1 | 100 | 400 | 100 | 100 | 1 | RW | 400027 | 0x03,0x06,0x10 | 400 | mSec
|  | EF ZSI | 0:OFF, 1:IN, 2:OUT,3: BOTH | 2 | 1 | 0 | 3 | 1 | 1 | 1 | RW | 400028 | 0x03,0x06,0x10 | 0 | -
| OverLoad (Neutral) Protection | Function | 0 : Protection Disable 1 : Alarm 2 : Trip 3 : Alarm + Trip | 2 | 1 | 0 | 3 | 1 | 1 | 1 | RW | 400029 | 0x03,0x06,0x10 | 0 | -
|  | Pickup IN = Ir x ... | 0.5 - 2 x Ir (Step: 0.05) | 2 | 1 | 50 | 200 | 5 | 5 | 1/100 | RW | 400030 | 0x03,0x06,0x10 | 100 | Ir (Amp)
|  | Prealarm | 0.5 - 0.95 x IN (Step: 0.05) | 2 | 1 | 50 | 95 | 5 | 5 | 1/100 | RW | 400031 | 0x03,0x06,0x10 | 80 | IN (Amp)
|  | Delay | 0:O/L curve | 2 | 1 | 0 | 0 | - | - | 1/10 | RW | 400032 | 0x03,0x06,0x10 | 0 | -
Current Protections (Set Group 2)
Current Protections (Set Group 2) | OverLoad Protection | Function | 0 : Protection Disable 1 : Alarm 2 : Trip 3 : Alarm + Trip | 2 | 1 | 0 | 3 | 1 | 1 | 1 | RW | 400251 | 0x03,0x06,0x10 | 0 | -
|  | Pickup (Ir) | 0.4 - 1 x In (Step: 0.01) | 2 | 1 | 40 | 100 | 1 | 1 | 1/100 | RW | 400252 | 0x03,0x06,0x10 | 60 | In (Amp)
|  | Prealarm | 0.5 - 0.95 x Ir (Step: 0.01) | 2 | 1 | 50 | 95 | 1 | 1 | 1/100 | RW | 400253 | 0x03,0x06,0x10 | 50 | Ir (Amp)
|  | Thermal Memory | 0:OFF, 20 min | 2 | 1 | 0 | 20 | - | - | 1 | RW | 400254 | 0x03,0x06,0x10 | 0 | -
|  | O/L Characteristic | 1: Extremely Inverse (I2T) 2: I Power 4 (I4T) 3: Very Inverse (VI) 4:Longtime Inverse (LI) 5: Standard Inverse (SI) | 2 | 1 | 1 | 5 | 1 | 1 | 1 | RW | 400255 | 0x03,0x06,0x10 | 0 | -
|  | Delay (@ 6 x Ir) | Range : 0.5, 1,2,4,6,12,18,24,30s. | 2 | 1 | 5 | 300 | - | - | 1/10 | RW | 400256 | 0x03,0x06,0x10 | 5 | Sec
| Short Circuit Protection | Function | 0 : Protection Disable 1 : Alarm 2 : Trip 3 : Alarm + Trip | 2 | 1 | 0 | 3 | 1 | 1 | 1 | RW | 400257 | 0x03,0x06,0x10 | 1 | -
|  | Double Selective | 0:Disable, 1:Enable | 2 | 1 | 0 | 1 | 1 | 1 | 1 | RW | 400258 | 0x03,0x06,0x10 | 0 | -
|  | Pickup High (Is) | 0.6 - 12 x In (Step of 0.05) | 2 | 1 | 60 | 1200 | 5 | 5 | 1/100 | RW | 400259 | 0x03,0x06,0x10 | 600 | In (Amp)
|  | Pickup Low (Is) | 0.6 - 12 x In (Step of 0.05) | 2 | 1 | 60 | 1200 | 5 | 5 | 1/100 | RW | 400260 | 0x03,0x06,0x10 | 600 | In (Amp)
|  | Prealarm | 0.5 - 0.95 x Is (Step: 0.05) | 2 | 1 | 50 | 95 | 5 | 5 | 1/100 | RW | 400261 | 0x03,0x06,0x10 | 50 | Is (Amp)
|  | I2T | 0:Disable, 1:Enable | 2 | 1 | 0 | 1 | 1 | 1 | 1 | RW | 400262 | 0x03,0x06,0x10 | 0 | -
|  | Delay High | 20-100-200-300-400ms | 2 | 1 | 20 | 400 | 80 | 100 | 1 | RW | 400263 | 0x03,0x06,0x10 | 400 | mSec
|  | Delay Low | 20-100-200-300-400ms | 2 | 1 | 20 | 400 | 80 | 100 | 1 | RW | 400264 | 0x03,0x06,0x10 | 400 | mSec
|  | Cold Load feature | 0:Disable, 1:Enable | 2 | 1 | 0 | 1 | 1 | 1 | 1 | RW | 400265 | 0x03,0x06,0x10 | 0 | -
|  | Cold Load Delay | 100ms to 10 Sec (Steps of 100ms) | 2 | 1 | 100 | 10000 | 100 | 100 | 1 | RW | 400266 | 0x03,0x06,0x10 | 1000 | mSec
|  | SC ZSI | 0:OFF, 1:IN, 2:OUT,3: BOTH | 2 | 1 | 0 | 3 | 1 | 1 | 1 | RW | 400267 | 0x03,0x06,0x10 | 0 | -
| Instantaneous Protection | Function | 0:Disable, 1:Enable | 2 | 1 | 0 | 1 | 1 | 1 | 1 | RW | 400268 | 0x03,0x06,0x10 | 1 | -
|  | Pickup | Range 1.5 In to 15 In 1.5 In to 10 In (Steps of 0.1 In) 10 In to 15 In (Steps of 1 In) | 2 | 1 | 15 | 150 | - | - | 1/10 | RW | 400269 | 0x03,0x06,0x10 | 1000 | In (Amp)
| Earth Fault Protection | Function | 0 : Protection Disable 1 : Alarm 2 : Trip 3 : Alarm + Trip | 2 | 1 | 0 | 3 | 1 | 1 | 1 | RW | 400270 | 0x03,0x06,0x10 | 0 | -
|  | Pickup (Ig) | 0.1 - 0.6 x In (Step 0.1) | 2 | 1 | 1 | 6 | 1 | 1 | 1/10 | RW | 400271 | 0x03,0x06,0x10 | 60 | In (Amp)
|  | Prealarm | 0.5 - 0.95 x Ig (Step: 0.05) | 2 | 1 | 50 | 95 | 5 | 5 | 1/100 | RW | 400272 | 0x03,0x06,0x10 | 80 | Ig (Amp)
|  | Cold Load feature | 0:Disable, 1:Enable | 2 | 1 | 0 | 1 | 1 | 1 | 1 | RW | 400273 | 0x03,0x06,0x10 | 0 | -
|  | Cold Load Delay | 100ms to 5 Sec (Steps of 100ms) | 2 | 1 | 100 | 5000 | 100 | 100 | 1 | RW | 400274 | 0x03,0x06,0x10 | 1000 | mSec
|  | E/F Characteristic (IDMT) | 0:Disable, 1:Enable | 2 | 1 | 0 | 1 | 1 | 1 | 1 | RW | 400275 | 0x03,0x06,0x10 | 0 | -
|  | IDMT Off Delay | 100ms to 1 Sec (Steps of 100ms) | 2 | 1 | 100 | 1000 | 100 | 100 | 1 | RW | 400276 | 0x03,0x06,0x10 | 400 | mSec
|  | IDMT On Delay | 100ms to 400ms (Steps of 100ms) | 2 | 1 | 100 | 400 | 100 | 100 | 1 | RW | 400277 | 0x03,0x06,0x10 | 400 | mSec
|  | EF ZSI | 0:OFF, 1:IN, 2:OUT,3: BOTH | 2 | 1 | 0 | 3 | 1 | 1 | 1 | RW | 400278 | 0x03,0x06,0x10 | 0 | -
| OverLoad (Neutral) Protection | Function | 0 : Protection Disable 1 : Alarm 2 : Trip 3 : Alarm + Trip | 2 | 1 | 0 | 3 | 1 | 1 | 1 | RW | 400279 | 0x03,0x06,0x10 | 0 | -
|  | Pickup IN = Ir x ... | 0.5 - 2 x Ir (Step: 0.05) | 2 | 1 | 50 | 200 | 5 | 5 | 1/100 | RW | 400280 | 0x03,0x06,0x10 | 100 | Ir (Amp)
|  | Prealarm | 0.5 - 0.95 x IN (Step: 0.05) | 2 | 1 | 50 | 95 | 5 | 5 | 1/100 | RW | 400281 | 0x03,0x06,0x10 | 80 | IN (Amp)
|  | Delay | 0:O/L curve | 2 | 1 | 0 | 0 | - | - | 1/10 | RW | 400282 | 0x03,0x06,0x10 | 0 | -
| Internal Temperature Protection | Function | 0 : Protection Disable 1 : Alarm (80 degree) 2 : Trip (105 degree) 3 : Alarm + Trip (105 degree) | 2 | 1 | 0 | 3 | 1 | 1 | 1 | RW | 400283 | 0x03,0x06,0x10 | 0 | - | Fixed Tripping delay - 30 sec
Note on C17: Interlocked with Instantaneous Pickup in SG1 Short Circuit Pickup High setting should be less than or equal to Instantaneous pickup setting.
Note on C18: Interlocked with Instantaneous Pickup in SG1 Short Circuit Pickup Low setting should be less than or equal to Instantaneous pickup setting.
Note on C61: Interlocked with Instantaneous Pickup in SG1 Short Circuit Pickup High setting should be less than or equal to Instantaneous pickup setting.
Note on C62: Interlocked with Instantaneous Pickup in SG1 Short Circuit Pickup Low setting should be less than or equal to Instantaneous pickup setting.

## Commands
| Can be added | [10 empty] | Data Sets
Register Access
| Attribute Name | Size (in Bits) | Min Value | Max Value | Step Size | Multiplier | R/W Access | Register Address | Function Codes | Default Value | Units
Commands
Reset Commands
Commands | Fault Counter | 1 | 0 | 1 | - | - | RW | 1 | 0x01,0x05,0x15 | 0 | -
| Breaker Operation Counter | 1 | 0 | 1 | - | - | RW | 2 | 0x01,0x05,0x15 | 0 | -
| Clear MD | 1 | 0 | 1 | - | - | RW | 3 | 0x01,0x05,0x15 | 0 | -
| Clear Demand Power | 1 | 0 | 1 | - | - | RW | 4 | 0x01,0x05,0x15 | 0 | -
| Clear Max Min Current Values | 1 | 0 | 1 | - | - | RW | 5 | 0x01,0x05,0x15 | 0 | -
| Clear Max Min Voltage Values | 1 | 0 | 1 | - | - | RW | 6 | 0x01,0x05,0x15 | 0 | -
| Clear Energy | 1 | 0 | 1 | - | - | RW | 7 | 0x01,0x05,0x15 | 0 | -
| Trip Fault Indication | 1 | 0 | 1 | - | - | RW | 8 | 0x01,0x05,0x15 | 0 | -
| Communication Statistics | 1 | 0 | 1 | - | - | RW | 9 | 0x01,0x05,0x15 | 0 | -
| Restore Factory Default Setting | 1 | 0 | 1 | - | - | RW | 10 | 0x01,0x05,0x15 | 0 | -
| Reset Contact Wear | 1 | 0 | 1 | - | - | RW | 11 | 0x01,0x05,0x16 | 1 | -
| Reset Service Hours | 1 | 0 | 1 | - | - | RW | 12 | 0x01,0x05,0x17 | 2 | -
Breaker Commands
| Breaker Open (Trip Breaker) | 1 | 0 | 1 | - | - | RW | 13 | 0x01,0x05,0x15 | 0 | -
| Breaker Close | 1 | 0 | 1 | - | - | RW | 14 | 0x01,0x05,0x15 | 0 | -
SetGroup Change
| Change Setting Group | 1 | 0 | 1 | - | - | RW | 15 | 0x01,0x05,0x15 | 0 | -
Acknowledge
| Breaker Maintenance Done | 1 | 0 | 1 | - | - | RW | 16 | 0x01,0x05,0x15 | 0 | -
| Breaker Maintenance Reject | 1 | 0 | 1 | - | - | RW | 17 | 0x01,0x05,0x15 | 0 | -
| Validate Password | 1 | 0 | 0 | - | - | RW | 18 | 0x01,0x05,0x15 | 0 | -
| Reserved | 1 | 0 | 0 | - | - | RW | 19 | 0x01,0x05,0x15 | 0 | -
| Reserved | 1 | 0 | 0 | - | - | RW | 20 | 0x01,0x05,0x15 | 0 | -
| Reserved | 1 | 0 | 0 | - | - | RW | 21 | 0x01,0x05,0x15 | 0 | -
| Reserved | 1 | 0 | 0 | - | - | RW | 22 | 0x01,0x05,0x15 | 0 | -